## Remodel Rack A (Part 1)
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | Existing | [12 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Laurel, DE |  |  |  | Rack Model: | 0 | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 1458 |  |  | Salesman |  | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY 7/23/19 |  |  | Prepared By: |  | Kim Austin |  | Date Originated |  |  | 2/17/05 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC-RMCC
[11 empty] | Line |  |  |  | 208 / 60 / 3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
[11 empty] | Control |  |  |  | 208 / 60 / 1 |  |  | Case Manufacturer |  |  |  | Tyler
[11 empty] | MCA | [6 empty] | A-12 Date:
Max. Overcurrent
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | MBTU | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
| SWEP | 0 |  |  | 0 | Low temp Subcooler | 67 | 36 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8 BV | PORT2 79
1 | 12'12' | 24' L4M |  |  | 1 | MD Fresh Meat 32.33 | 33 | 15 | HG 2 Wire | 1.8 | 120 | 7.8 | 1 | 216 | 936 | 120 | ME14S250 | 5/8 BV | SPT2 911 | 38 | 1 1/8 | 7/8 | 5/8
2 | 12' | L4M |  |  | 1 | MD Fresh Meat 31 | 16.5 | 15 | HG 2 Wire | 0.9 | 120 | 3.9 | 0.5 | 108 | 468 | 60 | ME14S250 | 5/8 BV | SPT2 79 | 38 | 7/8 | 7/8 | 5/8
3 | 8'8'8'8' | 32' LM/3 |  |  | 1 | Fresh Meat 24-30 | 19 | 15 | HG 2 Wire | 1.6 | 120 | 0 | 1.2 | 192 | 0 | 144 | ME14S250 | 5/8 BV | SPT2 79 | 84 | 7/8 | 7/8 | 5/8
4 | 796 sq.ft. | 2)SVA-100 |  | EXISTING | 0 | Meat Prep | 43.78 | 30 | Off Cycle | 3.6 | 120 | 0 | 0 | 414 | 0 | 0 | 0 | 5/8 BV | SPT2 1113 | 94 | 1 1/8 | 1 1/8 | 1/2
5 | 15x24x8.5 | AG46-164 |  | EXISTING | 1 | Meat Cooler | 18.3 | 20 | HG 2 Wire | 2 | 230/1 | 0 | 0 | 0 | 0 | 0 | ME14S250 | 5/8 BV | SPT2 79 | 133 | 1 1/8 | 7/8 | 5/8
6 | 15x24x8.5 | AA38-195 |  | EXISTING | 0 | Produce Cooler | 18.3 | 25 | Off Cycle | 3 | 120 | 0 | 0 | 345 | 0 | 0 | 0 | 5/8 BV | SPT2 79 | 133 | 7/8 | 7/8 | 1/2
7 | 22x33x10 | 2)FL26-67 |  | EXISTING | 0 | Produce Prep | 32.7 | 30 | Off Cycle | 2.4 | 120 | 0 | 0 | 276 | 0 | 0 | 0 | 5/8 BV | SPT2 911 | 177 | 1 1/8 | 1 1/8 | 1/2
8 | 12' | L6DL |  |  | 0 | Multi Deck Produce 21 | 17.1 | 20 | Off Cycle | 0.9 | 120 | 6.3 | 0 | 108 | 756 | 0 | 0 | 5/8 BV | SPT2 79 | 175 | 1 3/8 | 1 1/8 | 1/2
9 | 8'8'12' | 28' QHZVP1 |  |  | 0 | Produce 18-20 | 15 | 20 | Off Cycle | 1.4 | 115 | 4 | 0 | 168 | 480 | 0 | 0 | 5/8 BV | SPT2 79 | 118 | 1 1/8 | 7/8 | 1/2
10 | [5 empty] | SPARE |  |  | Off Cycle |  |  |  | 0 |  |  | 0 | 0 | 5/8 BV | SPT2 911
11 | 8'12'12'/12' | QHZVP/ O5DM |  |  | 0 | Produce/ MD Prod13-16 | 57.8 | 26 | Off Cycle | 4 | 115 | 4.7 | 0 | 480 | 564 | 0 | 0 | 5/8 BV | SPT2 1113 | 194 | 1 3/8 | 1 3/8 | 5/8
12 |  |  |  |  | 0 | SPARE |  |  | Off Cycle | [6 empty] | 0 | 0 | 5/8 BV | SPT2 59
13 | 12'12' | 24' L6DL |  |  | 0 | Lunch Meat 11,12 | 39 | 15 | HG 2 Wire | 1.8 | 120 | 12.6 |  | 216 | 1512 |  | ME14S250 | 5/8 BV | SPT2 1113 | 205 | 1 3/8 | 1 3/8 | 5/8
14 | 8'8' | 16' SSD/1 |  |  | 0 | Refrigerated Bakery 7-9 | 15.7 | 15 | Off Cycle | 1.2 | 120 | 3.6 | 3 | 144 | 432 | 360 | 0 | 5/8 BV | SPT2 79 | 179 | 1 1/8 | 7/8 | 5/8
15 | 8'8' | 16' LLM |  |  | 0 | Cold Deli 4-6 | 5.6 | 20 | Off Cycle | 0.8 | 120 | 2.4 | 2 | 96 | 288 | 240 | 0 | 5/8 BV | SPT2 59 | 194 | 5/8 | 1/2 | 1/2
16 | 7x14x8.5 | AA28-97 |  |  | 0 | Deli Cooler | 7.7 | 20 | Off Cycle | 2 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8 BV | SPT2 59 | 240 | 7/8 | 5/8 | 1/2
17 | 8'12'/1 | 20' L4MG |  |  | 0 | Self Serve Deli 1-3 | 31 | 15 | Off Cycle | 1.2 | 120 | 1.8 | 2 | 138 | 207 | 230 | 0 | 5/8 BV | SPT2 59 | 265 | 1 1/8 | 7/8 | 1/2
18 | 8'12'12'12' | 44' L6DL | Retrofit Doors |  | 0 | Beer (future) | 22 | 32 | Off Cycle | 3.3 | 120 | 22.3 | 0 | 396 | 2676 | 0 | 0 | 5/8 BV | SPT 1313 | 200 | 1 5/8 | 1 5/8 | 5/8
19 | 12'12' | 24' L6DL | Retrofit Doors |  | 0 | Dairy 44,45 | 12 | 30 | Off Cycle | 1.8 | 120 | 12.6 | 0 | 216 | 1512 | 0 | 0 | 5/8 BV | SPT2 1113 | 210 | 1 3/8 | 1 3/8 | 1/2
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  |  | Compressor | Comp |  | Cap | Suct |  |  |  |  | Suction |  |  | Capacity | Circuit |  | Wire Size | Model #
Condensing Temp |  |  |  | Group # | # | Compressor | MBTU | ° F | HP | RPM | RLA | LRA | Filter |  |  | Control | Breaker | Contactor | (AWG) | T.D.
Outside Air Temp. | [19 empty] | F P I
Required MBTUH Group 1 |  |  | 0 | [16 empty] | Voltage
Comp. Capac. MBTUH Group 1 |  |  | 0 | [16 empty] | FLA
Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA
% Loaded Group 1 | [19 empty] | MOPD
Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight
|  |  | 0 | [16 empty] | Size
Required MBTUH Group 2 |  |  | 0 | [16 empty] | # of Fans
Comp. Capac. MBTUH Group 2 |  |  | 0 | [16 empty] | Line To
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From
% Loaded Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve - Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
Comp. Capac. MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Group 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Loaded Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil type |  |  |  | Attron | [5 empty] | Receiver H / V |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Dia. x Length |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 0 |  | Reservoir Capacity |  |  |  | Subcooler | [5 empty] | Lbs @ 90% PD |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter Main / Ind |  |  |  | Liquid Temp Out | [9 empty] | C P R
Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight | [5 empty] | CONDENSER TO BE 50%/50% SPLIT DUAL HEADER

## Remodel Rack A (Part 2)
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | Existing | [12 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Laurel, DE |  |  |  | Rack Model: | Existing | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 1458 |  |  | Salesman |  | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY 7/23/19 |  |  | Prepared By: |  | Kim Austin |  | Date Originated |  |  | 2/17/05 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC-RMCC
[11 empty] | Line |  |  |  | 208 / 60 / 3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
[11 empty] | Control |  |  |  | 208 / 60 / 1 |  |  | Case Manufacturer |  |  |  | Tyler
[11 empty] | MCA |  |  |  | 422 |  |  | A-12 Date:
[11 empty] | Max. Overcurrent |  |  |  | 500
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | MBTUH | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
20 | 12'12'12' | 36' L6DL | Retrofit Doors |  | 0 | Dairy 41-43 | 18 | 30 | Off Cycle | 2.7 | 120 | 18.9 | 0 | 324 | 2268 | 0 | 0 | 5/8 BV | SPT2 1113 | 172 | 1 3/8 | 1 3/8 | 5/8
21 | 12' | L6DL | Retrofit Doors |  | 1 | Dairy 39 | 6 | 30 | Off Cycle | 0.9 | 120 | 6.3 | 0 | 108 | 756 | 0 | ME14S250 | 5/8 BV | SPT2 911 | 136 | 1 1/8 | 7/8 | 5/8
22 | 12' | L6DL | Retrofit Doors |  | 0 | Dairy 40 | 6 | 30 | Off Cycle | 0.9 | 120 | 6.3 | 0 | 108 | 756 | 0 | 0 | 5/8 BV | SPT2 79 | 130 | 7/8 | 7/8 | 1/2
23 | 8'8' | 16' L6DLR | Retrofit Doors |  | 0 | Rear Load Dairy 37,38 | 8 | 30 | Off Cycle | 1.2 | 120 | 6.8 | 0 | 144 | 816 | 0 | 0 | 5/8 BV | SPT2 911 | 83 | 1 1/8 | 7/8 | 5/8
24 | 13x36x8.5 | 2)AA28-134 |  | EXISTING | 0 | Dairy Cooler | 26.7 | 20 | Off Cycle | 4 | 120 | 0 | 0 | 460 | 0 | 0 | 0 | 5/8 BV | SPT2 911 | 87 | 1 1/8 | 1 1/8 | 1/2
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | Existing |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R407A | Compressor | Comp |  | Cap | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | VAC 158
Condensing Temp |  |  | 115 | Group # | # | Compressor | MBTU | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 15
Outside Air Temp. |  |  | 100 |  | 1 | 4DK3R22ME | 143.75 | 15 | 25 |  | 82.2 |  |  |  |  | UNLD | 125A | 90A | #1 | F P I |  | 10
Required MBTUH Group 1 |  |  | 536.2 |  | 2 | 4DH3-250L | 143.75 | 15 | 25 |  | 82.2 | [5 empty] | 125A | 90A | #1 | Voltage |  | 208 / 3
Comp. Capac. MBTUH Group 1 |  |  | 799.6 |  | 3 | 4DR3R28ME | 170.7 | 15 | 30 |  | 94 |  |  |  |  | 0 | 125A | 0 | #1 | FLA |  | 64
Effective capac. with subcooling |  |  | 799.6 |  | 4 | 4DJ3-300J | 170.7 | 15 | 30 |  | 94 |  |  |  |  | 0 | 125A | 0 | #1 | MCA |  | 65.6
% Loaded Group 1 |  |  | 67.06% |  | 5 | 4DR3R28ME | 170.7 | 15 | 30 |  | 94 |  |  |  |  | 0 | 125A | 0 | #1 | MOPD |  | 80
Rej. Heat (MBH) Group 1 |  |  | 1143.428 | [16 empty] | Weight |  | 2800
|  |  | 0 | [16 empty] | Size |  | 96"X242"
Required MBTUH Group 2 |  |  | 0 |  |  |  |  | 0 | [11 empty] | # of Fans |  | 2x5
Comp. Capac. MBTUH Group 2 |  |  | 0 | [16 empty] | Line To |  | 2)2 1/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2)1 5/8
% Loaded Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5202 |  | Drain Regulator |  |  | -- |  |  | Air reclaim |  | 16D17B |  | Head Fan LT/MT |  | NO
|  |  | 0 |  | Oil Separator -- Group 2 |  | S-5294 |  | Master Solenoid |  |  | -- |  |  | Water Reclaim |  | -- |  | Crankcase Htrs. |  | NO
Required MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve - Grp 1 |  | MS-34 |  | Surge Solenoid |  |  | ME42S2130 |  |  | Line size To |  | 2 5/8
Comp. Capac. MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  | MS-26 |  | Surge Ball Valve |  |  | -- |  |  | Line size From |  | 2 5/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  | DDR-20 |  | Surge Check |  |  | -- |  |  | Bypass Valve |  | -- |  | Suction Crossover / Load Shed
% Loaded Group 3 |  |  |  |  | Bypass Regulator |  | -- |  | Surge Style |  |  | BYPASS |  |  | Split Cond. Valve |  | 16D17B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil type |  | MINERAL |  | Attron |  |  | -- |  |  | Receiver H / V |  | VERTICAL |  | Ball Valve
|  |  | 0 |  | Brand / Number |  | -- | [7 empty] | Dia. x Length |  | 20" X 60" |  | Check Valve
Total Rej. Heat (MBH) |  |  | 1143.428 |  | Reservoir Capacity |  | 2 GAL. |  | Subcooler |  |  | -- |  |  | Lbs @ 90% PD |  | 610 |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 571.714 |  | Suction Filter Main / Ind |  | (2)5CFA-50S |  | Liquid Temp Out |  |  | -- | [6 empty] | C P R
Compressor Capacity (Tons) |  |  | 66.6333 |  | Drier |  | C-19213 |  | TEV |  |  | -- | [6 empty] | From / To
Rack Size |  |  | 175x36x78
Estimated Rack Weight |  |  | 4400 |  |  | CONDENSER TO BE 50%/50% SPLIT DUAL HEADER

## Remodel Rack B (Part 3)
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack B | Existing | [12 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Laurel, DE |  |  |  | Rack Model: | Existing | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 1458 |  |  | Salesman |  | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY 7/23/19 |  |  | Prepared By: |  | Kim Austin |  | Date Originated |  |  | 2/17/05 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC-RMCC
[11 empty] | Line |  |  |  | 208 / 60 / 3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
[11 empty] | Control |  |  |  | 208 / 60 / 1 |  |  | Case Manufacturer |  |  |  | Tyler
[11 empty] | MCA |  |  |  | 299.5 |  |  | A-12 Date:
[11 empty] | Max. Overcurrent |  |  |  | 350
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | MBTUH | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
1 | 10x11x8.5 | AG36-120 |  | EXISTING | 1 | Meat Freezer | 10.4 | -15 | HG 2 Wire | 1.5 | 230/1 | 0 | 0 | 0 | 0 | 0 | ME14S250 | ME14S250 | SPT2 79 | 115 | 1 1/8 | 7/8 | 5/8
2 | 3 | L5FG |  |  | 1 | Frozen Bakery 10 | 4.9 | -18 | HG 2 Wire | 1.3 | 120 | 2.9 | 4.7 | 156 | 348 | 564 | ME14S250 | 5/8 BV | SPT2 59 | 265 | 7/8 | 5/8 | 5/8
3 | 12x18x8.5 | AG46-164 |  | EXISTING | 1 | Bakery Freezer | 14.8 | -11 | HG 2 Wire | 2 | 230/1 | 0 | 0 | 0 | 0 | 0 | ME14S250 | ME14S250 | SPT2 79 | 209 | 1 1/8 | 1 1/8 | 5/8
4 | 8'8' | LFW |  |  | 0 | Meat Promo 22,23 | 7.2 | -18 | HG 2 Wire | 0.8 | 120 | 0 | 3.6 | 96 | 0 | 432 | ME14S250 | 5/8 BV | SPT2 59 | 100 | 7/8 | 7/8 | 5/8
5 | 5,5,4 | 14Dr L5FG |  |  | 1 | Frozen Food/Meat 34-36 | 23 | -11 | HG 2 Wire | 5.5 | 120 | 12.3 | 21.8 | 660 | 1476 | 2616 | ME14S250 | 5/8 BV | SPT2 911 | 55 | 1 3/8 | 1 3/8 | 5/8
6 | 5,5 | 10Dr L5FG |  |  | 1 | Frozen Food 61,62 | 16.4 | -11 | HG 2 Wire | 4 | 120 | 8.6 | 15.6 | 480 | 1032 | 1872 | ME14S250 | 5/8 BV | SPT2 79 | 95 | 1 1/8 | 1 1/8 | 5/8
7 | 5,5 | 10Dr L5FG |  |  | 1 | Frozen Food 63,64 | 16.4 | -11 | HG 2 Wire | 4 | 120 | 8.6 | 15.6 | 480 | 1032 | 1872 | ME14S250 | 5/8 BV | SPT2 79 | 130 | 1 1/8 | 1 1/8 | 5/8
8 | 5,5,3 | 13Dr L5FG |  |  | 1 | Frozen Food 65-67 | 21.3 | -11 | HG 2 Wire | 5.3 | 120 | 11.5 | 20.3 | 636 | 1380 | 2436 | ME14S250 | 5/8 BV | SPT2 911 | 165 | 1 3/8 | 1 1/8 | 5/8
9 | 5,5,5 | 15Dr L5FG |  |  | 1 | Frozen Food 58-60 | 24.6 | -11 | HG 2 Wire | 6 | 120 | 12.9 | 23.4 | 720 | 1548 | 2808 | ME14S250 | 5/8 BV | SPT2 911 | 185 | 1 3/8 | 1 3/8 | 5/8
10 | 5,5 | 10Dr L5FG |  |  | 1 | Frozen Food 56,57 | 16.4 | -11 | HG 2 Wire | 4 | 120 | 8.6 | 15.6 | 480 | 1032 | 1872 | ME14S250 | 5/8 BV | SPT2 79 | 150 | 1 1/8 | 1 1/8 | 5/8
11 | 5 | L5FG |  |  | 1 | Frozen Food 55 | 8.8 | -11 | HG 2 Wire | 2 | 120 | 4.3 | 7.8 | 240 | 516 | 936 | ME14S250 | 5/8 BV | SPT2 79 | 130 | 1 1/8 | 1 1/8 | 5/8
12 | 3,3,3 | 9Dr L5FG |  |  | 1 | Frozen Food 52-54 | 14.7 | -18 | HG 2 Wire | 3.9 | 120 | 8.7 | 14.1 | 468 | 1044 | 1692 | ME14S250 | 5/8 BV | SPT2 79 | 135 | 1 3/8 | 1 3/8 | 5/8
13 | 5,5,5 | 15Dr L5FG |  |  | 1 | Ice Cream 49-51 | 26.4 | -18 | HG 2 Wire | 6 | 120 | 12.9 | 23.4 | 720 | 1548 | 2808 | ME14S250 | 5/8 BV | SPT2 1113 | 165 | 1 3/8 | 1 3/8 | 5/8
14 | 5,4,3 | 12Dr L5FG |  |  | 1 | Ice Cream 46-48 | 21.1 | -18 | HG 2 Wire | 4.8 | 120 | 10.9 | 18.7 | 576 | 1308 | 2244 | ME14S250 | 5/8 BV | SPT2 911 | 185 | 1 3/8 | 1 3/8 | 5/8
15 | 12x35x8.5 | 2)AG36-120 |  | EXISTING | 1 | Storage Freezer | 25 | -15 | HG 2 Wire | 3 | 230/1 | 0 | 0 | 0 | 0 | 0 | ME14S250 | ME14S250 | SPT2 911 | 94 | 1 1/8 | 1 1/8 | 5/8
16 | 12'X15'X8.5 | AG54-180 |  | EXISTING | 1 | Ice Cream Freezer | 13.65 | -18 | HG 2 Wire | 2.5 | 230/1 | 0 | 0 | 0 | 0 | 0 | ME14S250 | ME14S250 | SPT2 79 | 123 | 1 1/8 | 1 1/8 | 5/8
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | Existing |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R407A | Compressor | Comp |  | Cap | Suct |  |  |  |  | Suction |  |  | Capacity | Circuit |  | Wire Size | Model # |  | VAC 95
Condensing Temp |  |  | 110 | Group # | # | Compressor | MBTU | ° F | HP | RPM | RLA | LRA | Filter |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 9.74
Outside Air Temp. |  |  | 100 | 1 | 1 | 4DS3F76KE | 68.18 | -20 | 22 |  | 66 |  |  |  |  | UNLD | 90A | 75A | #3 | F P I |  | 10
Required MBTUH Group 1 |  |  | 265.05 | 1 | 2 | 4DS3F76KE | 68.18 | -20 | 22 |  | 66 |  |  |  |  | UNLD | 90A | 75A | #3 | Voltage |  | 208 / 3
Comp. Capac. MBTUH Group 1 |  |  | 272.72 | 1 | 3 | 4DT3F76KE | 68.18 | -20 | 22 |  | 66 |  |  |  |  | 0 | 90A | 75A | #3 | FLA |  | 38.4
Effective capac. with subcooling |  |  | 362.7176 | 1 | 4 | 4DT3-220L | 68.18 | -20 | 22 |  | 66 |  |  |  |  | 0 | 90A | 75A | #3 | MCA |  | 40
% Loaded Group 1 |  |  | 73.07% | [16 empty] | MOPD |  | 50
Rej. Heat (MBH) Group 1 |  |  | 455.4424 | [16 empty] | Weight |  | 1840
|  |  | 0 | [16 empty] | Size |  | 96"X146"
Required MBTUH Group 2 |  |  | 0 | [16 empty] | # of Fans |  | 6
Comp. Capac. MBTUH Group 2 |  |  | 0 | [16 empty] | Line To |  | 2)1 3/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2)1 1/8
% Loaded Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5294 |  | Drain Regulator |  |  | -- |  |  | Air reclaim |  | 12D13B |  | Head Fan LT/MT |  | YES
|  |  | 0 |  | Oil Separator -- Group 2 |  | -- |  | Master Solenoid |  |  | -- |  |  | Water Reclaim |  | 12D13B |  | Crankcase Htrs. |  | NO
Required MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve - Grp 1 |  | MS-26 |  | Surge Solenoid |  |  | ME25S290 |  |  | Line size To |  | 1 5/8
Comp. Capac. MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Group 2 |  | -- |  | Surge Ball Valve |  |  | -- |  |  | Line size From |  | 1 5/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  | DDR-20 |  | Surge Check |  |  | -- |  |  | Bypass Valve |  | 10# (WATER) |  | Suction Crossover / Load Shed
% Loaded Group 3 |  |  |  |  | Bypass Regulator |  | -- |  | Surge Style |  |  | BYPASS |  |  | Split Cond. Valve |  | 12D13B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil type |  | MINERAL |  | Attron |  |  | -- |  |  | Receiver H / V |  | VERTICAL |  | Ball Valve
|  |  | 0 |  | Brand / Number |  | -- | [7 empty] | Dia. x Length |  | 16" X 60" |  | Check Valve
Total Rej. Heat (MBH) |  |  | 455.4424 |  | Reservoir Capacity |  | 2 GAL. |  | Subcooler |  |  | B10 X 30 |  |  | Lbs @ 90% PD |  | 390 |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 227.7212 |  | Suction Filter Main / Ind |  | (2)4CFA-42S |  | Liquid Temp Out |  |  | 50 F | [6 empty] | C P R
Compressor Capacity (Tons) |  |  | 22.7267 |  | Drier |  | C-969 |  | TEV |  |  | EBFVE-C-C | [6 empty] | From / To
Rack Size |  |  | 140x36x78
Estimated Rack Weight |  |  | 4200 |  |  | CONDENSER TO BE 50%/50% SPLIT DUAL HEADER