## Remodel Rack A (Part 1)
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | Existing | [12 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Laurel, DE |  |  |  | Rack Model: | 0 | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 1458 |  |  | Salesman |  | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | 708620 |  |  | Prepared By: |  | Kim Austin |  | Date Originated |  |  | 2/17/05 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC-RMCC
APR | 7/23/19 | Kim Austin | Revised for remodel | [7 empty] | Line |  |  |  | 208 / 60 / 3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
APR1 | 9/4/19 | Kim Austin | Updated per walk through notes | [7 empty] | Control |  |  |  | 208 / 60 / 1 |  |  | Case Manufacturer |  |  |  | Tyler
B | 9/17/2019 | RFF | Updated case numbers | [7 empty] | MCA | [6 empty] | A-12 Date:
Max. Overcurrent
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | MBTU | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
| SWEP | 0 |  |  | 0 | Low temp Subcooler | 67 | 36 | NONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8 BV | PORT2 79
1 | [5 empty] | SPARE |  |  | Off Cycle | [8 empty] | 5/8 BV | SPT2 911
2 | 8'12'12' | 32' SANTIAGO |  |  | 1 | Lunch Meat N26-N28 | 8.74 | 27 | Off Cycle | 1.21 | 115 | 2.29 | 3.3 | 139.15 | 263.35 | 379.5 |  | 5/8 BV | SPT2 79 | 38 | 7/8 | 7/8 | 5/8
3 | 8'8'8'8'8' | 40' LSB |  |  | 1 | MD Fresh Meat N21-N25 | 60.32 | 23 | Off Cycle | 6.9 | 115 | 9.75 | 0 | 793.5 | 1121.25 |  |  | 5/8 BV | SPT 1313 | 40 | 1 3/8 | 1 3/8 | 5/8
4 | 796 sq.ft. | 2)SVA-100 |  | EXISTING | 0 | Meat Prep | 43.78 | 30 | Off Cycle | 3.6 | 115 | 0 | 0 | 414 | 0 | 0 |  | 5/8 BV | SPT2 1113 | 94 | 1 1/8 | 1 1/8 | 1/2
5 | 15x24x8.5 | RL6A330 |  | NEW | 1 | Meat Cooler | 18.3 | 28 | Off Cycle | 4.8 | 115 | 0 | 0 | 0 | 0 | 0 |  | 5/8 BV | SPT2 79 | 133 | 1 1/8 | 7/8 | 5/8
6 | 15x24x8.5 | RL6A295 |  | NEW | 0 | Produce Cooler | 18.3 | 28 | Off Cycle | 3.2 | 115 | 0 | 0 | 345 | 0 | 0 |  | 5/8 BV | SPT2 79 | 133 | 7/8 | 7/8 | 1/2
7 | 22x33x10 | 2)FL26-67 |  | EXISTING | 0 | Produce Prep | 32.7 | 30 | Off Cycle | 2.4 | 115 | 0 | 0 | 276 | 0 | 0 |  | 5/8 BV | SPT2 911 | 177 | 1 1/8 | 1 1/8 | 1/2
8 | 8'8'12' | 28' LSB |  |  | 1 | MD Fresh Meat N15-N17 | 42.22 | 23 | Off Cycle | 4.6 | 115 | 6.55 | 0 | 529 | 753.25 |  |  | 5/8 BV | SPT2 1113 | 150 | 1 3/8 | 1 1/8 | 5/8
9 | 8'8'/12' | 16' DX6LN/12'DX6LD |  |  | 1 | Produce/Doors N12-N14 | 22.5 | 28 | Off Cycle | 0.8 | 115 | 4.2 | 1.8 | 92 | 483 | 207 |  | 5/8 BV | SPT2 79 | 118 | 1 1/8 | 7/8 | 1/2
10 | [5 empty] | SPARE |  |  | Off Cycle |  |  |  | 0 |  |  | 0 |  | 5/8 BV | SPT2 911
11 | 8'12'12'/4' | 32' DX6LN/4'PF |  |  | 1 | Produce/Floral N08-N11 | 41.7 | 28 | Off Cycle | 1.3 | 115 | 5.3 | 0 | 149.5 | 609.5 | 0 |  | 5/8 BV | SPT2 1113 | 220 | 1 3/8 | 1 3/8 | 5/8
12 |  |  |  |  | 0 | SPARE |  |  | Off Cycle | [6 empty] | 0 |  | 5/8 BV | SPT2 59
13 |  |  |  |  | 0 | SPARE |  |  | Off Cycle | [8 empty] | 5/8 BV | SPT2 1113
14 |  |  |  |  | 0 | SPARE |  |  | Off Cycle | [7 empty] | 0 | 5/8 BV | SPT2 79
15 |  |  |  |  | 0 | SPARE |  |  | Off Cycle | [7 empty] | 0 | 5/8 BV | SPT2 59
16 | 7x14x8.5 | RL6A130 |  | NEW | 0 | Deli Cooler | 7.7 | 28 | Off Cycle | 2 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 5/8 BV | SPT2 59 | 240 | 7/8 | 7/8 | 1/2
17 | 6'8'12'8'12'12' | PT,PT,PTD,PT,PT,PT |  |  | 0 | Deli/Bakery N01-N06 | 56.4 | 26 | Off Cycle | 8.75 | 120 | 16.4 |  | 1006.25 | 1886 | 0 | 0 | 5/8 BV | SPT 1313 | 280 | 1 5/8 | 1 3/8 | 7/8
18 |  |  |  |  | 0 | SPARE |  |  | Off Cycle | [6 empty] | 0 | 0 | 5/8 BV | SPT 1313
19 | 8'8'12'12'12' | 52' DX6LD |  |  | 1 | Dairy Doors N38-N42 | 15.444 | 28 | Off Cycle | 1.6 | 115 | 8.34 | 7.9 | 184 | 959.1 | 908.5 | 0 | 5/8 BV | SPT2 1113 | 210 | 1 1/8 | 7/8 | 1/2
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  |  | Compressor | Comp |  | Cap | Suct |  |  |  |  | Suction |  |  | Capacity | Circuit |  | Wire Size | Model #
Condensing Temp |  |  |  | Group # | # | Compressor | MBTU | ° F | HP | RPM | RLA | LRA | Filter |  |  | Control | Breaker | Contactor | (AWG) | T.D.
Outside Air Temp. | [19 empty] | F P I
Required MBTUH Group 1 |  |  | 0 | [16 empty] | Voltage
Comp. Capac. MBTUH Group 1 |  |  | 0 | [16 empty] | FLA
Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA
% Loaded Group 1 | [19 empty] | MOPD
Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight
|  |  | 0 | [16 empty] | Size
Required MBTUH Group 2 |  |  | 0 | [16 empty] | # of Fans
Comp. Capac. MBTUH Group 2 |  |  | 0 | [16 empty] | Line To
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From
% Loaded Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve - Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
Comp. Capac. MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Group 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Loaded Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil type |  |  |  | Attron | [5 empty] | Receiver H / V |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Dia. x Length |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 0 |  | Reservoir Capacity |  |  |  | Subcooler | [5 empty] | Lbs @ 90% PD |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter Main / Ind |  |  |  | Liquid Temp Out | [9 empty] | C P R
Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight | [5 empty] | CONDENSER TO BE 50%/50% SPLIT DUAL HEADER

## Remodel Rack A (Part 2)
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | Existing | [12 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Laurel, DE |  |  |  | Rack Model: | Existing | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 1458 |  |  | Salesman |  | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | 708620 |  |  | Prepared By: |  | Kim Austin |  | Date Originated |  |  | 2/17/05 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC-RMCC
APR | 7/23/19 | Kim Austin | Revised for remodel | [7 empty] | Line |  |  |  | 208 / 60 / 3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
APR1 | 9/4/19 | Kim Austin | Updated per walk through notes | [7 empty] | Control |  |  |  | 208 / 60 / 1 |  |  | Case Manufacturer |  |  |  | Tyler
B | 9/17/2019 | RFF | Updated case numbers | [7 empty] | MCA |  |  |  | 385.7 |  |  | A-12 Date:
[11 empty] | Max. Overcurrent |  |  |  | 450 | NEW BREAKER
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | MBTUH | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
20 | 5) 12' | 60' DX6LD |  |  | 1 | Dairy Doors N33-N37 | 17.8 | 28 | Off Cycle | 2 | 115 | 9.1 | 9.1 | 230 | 1046.5 | 1046.5 | 0 | 5/8 BV | SPT2 1113 | 120 | 1 1/8 | 7/8 | 1/2
21 | 4' | 4'QD6L |  |  | 1 | Dairy Promo N51 | 5.54 | 23 | Off Cycle | 0.25 | 115 | 0.46 | 0 | 28.75 | 52.9 | 0 |  | 5/8 BV | SPT2 911 | 100 | 7/8 | 7/8 | 1/2
22 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 | 0 | 5/8 BV | SPT2 79
23 | [5 empty] | SPARE |  |  | Off Cycle | [6 empty] | 0 | 0 | 5/8 BV | SPT2 911
24 | 13x36x8.5 | 2)RL6A235 |  | NEW | 0 | Dairy Cooler | 26.7 | 28 | Off Cycle | 6.4 | 115 | 0 | 0 | 736 | 0 | 0 | 0 | 5/8 BV | SPT2 911 | 87 | 1 1/8 | 1 1/8 | 1/2
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | Existing |  |  | Compressor Specifications | [10 empty] | NEW | Condenser
Refrigerant Type |  |  | R407A | Compressor | Comp |  | Cap | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | RDD063
Condensing Temp |  |  | 115 | Group # | # | Compressor | MBTU | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 14.9
Outside Air Temp. |  |  | 100 |  | 1 | 4DK3R22ME | 163.9 | 20 | 25 |  | 82.2 |  |  |  |  | UNLD | 125A | 90A | #1 | F P I |  | 10
Required MBTUH Group 1 |  |  | 536.2 | NEW | 2 | 2DC3R53KL;-TFC-441 | 35.31 | 20 | 4 |  | 22.3 | [5 empty] | 30A | 30A | #10 | Voltage |  | 208 / 3
Comp. Capac. MBTUH Group 1 |  |  | 658.99 |  | 3 | 4DR3R28ME | 193.3 | 20 | 30 |  | 94 |  |  |  |  | 0 | 125A | 0 | #1 | FLA |  | 40
Effective capac. with subcooling |  |  | 658.99 | NEW | 4 | 3DA3R10ML-TFC-441 | 73.18 | 20 | 6.5 |  | 41 |  |  |  |  | 0 | 60A | 50A | #1 | MCA |  | 41
% Loaded Group 1 |  |  | 81.37% |  | 5 | 4DR3R28ME | 193.3 | 20 | 30 |  | 94 |  |  |  |  | 0 | 125A | 0 | #1 | MOPD |  | 45
Rej. Heat (MBH) Group 1 |  |  | 942.3557 | [16 empty] | Weight |  | 4125
|  |  | 0 | [16 empty] | Size |  | 9075"X242"
Required MBTUH Group 2 |  |  | 0 |  |  | CHANGE 4DH3-250L TO 2DD3R63KL-TFC-441 | [13 empty] | # of Fans |  | 10
Comp. Capac. MBTUH Group 2 |  |  | 0 |  |  | CHANGE 4DJ3-300J TO 3DA3R10ML-TFC-441 | [13 empty] | Line To |  | 2)2 1/8
Effective capac. with subcooling |  |  | 0 |  |  | TIE DISCHARGE HEADERS TOGTHER PIPE THROUGH S-5202 | [13 empty] | Line From |  | 2)1 5/8
% Loaded Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5202 | FLOAT | Drain Regulator |  |  | -- |  |  | Air reclaim |  | 16D17B |  | Head Fan LT/MT |  | NO
|  |  | 0 |  | Oil Separator -- Group 2 |  | S-5294 | REMOVE | Master Solenoid |  |  | -- |  |  | Water Reclaim |  | -- |  | Crankcase Htrs. |  | NO
Required MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve - Grp 1 |  | MS-34 |  | Surge Solenoid |  |  | REMOVE |  |  | Line size To |  | 2 5/8
Comp. Capac. MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  | MS-26 |  | Surge Ball Valve |  |  | 1 5/8 |  |  | Line size From |  | 2 5/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check |  |  | -- |  |  | Bypass Valve |  | -- |  | Suction Crossover / Load Shed
% Loaded Group 3 |  |  |  |  | Bypass Regulator |  | -- |  | Surge Style |  |  | BYPASS |  |  | Split Cond. Valve |  | 16D17B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil type |  | MINERAL |  | Attron |  |  | -- |  |  | Receiver H / V |  | VERTICAL |  | Ball Valve
|  |  | 0 |  | Brand / Number |  | -- | [7 empty] | Dia. x Length |  | 20" X 60" |  | Check Valve
Total Rej. Heat (MBH) |  |  | 942.3557 |  | Reservoir Capacity |  | 2 GAL. |  | Subcooler |  |  | -- |  |  | Lbs @ 90% PD |  | 610 |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 471.1778 |  | Suction Filter Main / Ind |  | (2)5CFA-50S |  | Liquid Temp Out |  |  | -- |  |  | PUMP OUT KIT |  | ADD |  | C P R
Compressor Capacity (Tons) |  |  | 54.9158 |  | Drier |  | C-19213 |  | TEV |  |  | -- | [6 empty] | From / To
Rack Size |  |  | 175x36x78
Estimated Rack Weight |  |  | 4400 |  |  | CONDENSER TO BE 50%/50% SPLIT DUAL HEADER

## Remodel Rack B (Part 3)
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack B | Existing | [12 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Laurel, DE |  |  |  | Rack Model: | Existing | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 1458 |  |  | Salesman |  | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | 708620 |  |  | Prepared By: |  | Kim Austin |  | Date Originated |  |  | 2/17/05 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC-RMCC
APR | 7/23/19 | Kim Austin | Revised for remodel | [7 empty] | Line |  |  |  | 208 / 60 / 3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
APR1 | 9/4/19 | Kim Austin | Updated per walk through notes | [7 empty] | Control |  |  |  | 208 / 60 / 1 |  |  | Case Manufacturer |  |  |  | Tyler
B | 9/17/2019 | RFF | Updated case numbers | [7 empty] | MCA |  |  |  | 261.9 |  |  | A-12 Date:
[11 empty] | Max. Overcurrent |  |  |  | 300 | NEW BREAKER
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | MBTUH | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
1 | 10x11x8.5 | AG36-120 |  | EXISTING | 1 | Meat Freezer | 10.4 | -15 | HG 2 Wire | 1.5 | 230/1 | 0 | 0 | 0 | 0 | 0 | ME14S250 | ME14S250 | SPT2 79 | 115 | 1 1/8 | 7/8 | 5/8
2 | 4 | QIV5V14 |  |  | 1 | Frozen Bakery N07 | 5.704 | -18 | HG 2 Wire | 0.84 | 115 | 0.6 | 3.35 | 96.6 | 69 | 385.25 | ME14S250 | 5/8 BV | SPT2 59 | 265 | 7/8 | 7/8 | 5/8
3 | 12x18x8.5 | AG46-164 |  | EXISTING | 1 | Bakery Freezer | 14.8 | -11 | HG 2 Wire | 2 | 230/1 | 0 | 0 | 0 | 0 | 0 | ME14S250 | ME14S250 | SPT2 79 | 209 | 1 1/8 | 1 1/8 | 5/8
4 | 6'6'6' | 18' BILBAO |  |  | 1 | Meat Promo N18-N20 | 7.47 | -18 | HG 2 Wire | 1.8 | 115 | 0 | 3.48 | 207 | 0 | 400.2 | ME14S250 | 5/8 BV | SPT2 59 | 100 | 1 1/8 | 7/8 | 5/8
5 | 5,5,5,5 | 20Dr QIV5V14 |  |  | 1 | F.F./F.Meat/Seafood N29-N32 | 26.6 | -11 | HG 2 Wire | 4.2 | 115 | 3 | 19.8 | 483 | 345 | 2277 | ME14S250 | 5/8 BV | SPT2 1113 | 40 | 1 3/8 | 1 3/8 | 5/8
6 | 3,3 | 6Dr QIV5V14 |  |  | 1 | Ice Cream/FF Ends N59,N67 | 8.556 | -18 | HG 2 Wire | 1.26 | 115 | 0.9 | 5.42 | 144.9 | 103.5 | 623.3 | ME14S250 | 5/8 BV | SPT2 79 | 95 | 1 1/8 | 7/8 | 5/8
7 | 5,5,4,3 | 14Dr QIV5V14 |  |  | 1 | Frozen Food N60-N63 | 22.5 | -11 | HG 2 Wire | 3.5 | 115 | 2.6 | 16 | 402.5 | 299 | 1840 | ME14S250 | 5/8 BV | SPT2 1113 | 130 | 1 3/8 | 1 1/8 | 5/8
8 | 5,5,5 | 15Dr QIV5V14 |  |  | 1 | Frozen Food N64-N66 | 19.875 | -11 | HG 2 Wire | 3.15 | 115 | 2.25 | 14.91 | 362.25 | 258.75 | 1714.65 | ME14S250 | 5/8 BV | SPT2 1113 | 100 | 1 3/8 | 1 1/8 | 5/8
9 | 5,5,3,3 | 16Dr QIV5V14 |  |  | 1 | Frozen Food N55-N58 | 21.2 | -11 | HG 2 Wire | 3.78 | 115 | 2.4 | 15.36 | 434.7 | 276 | 1766.4 | ME14S250 | 5/8 BV | SPT2 1113 | 160 | 1 3/8 | 1 3/8 | 5/8
10 | 5,5,5 | 15Dr QIV5V14 |  |  | 1 | Frozen Food N52-N54 | 19.875 | -11 | HG 2 Wire | 3.15 | 115 | 2.25 | 14.91 | 362.25 | 258.75 | 1714.65 | ME14S250 | 5/8 BV | SPT2 1113 | 120 | 1 3/8 | 1 1/8 | 5/8
11 | [5 empty] | SPARE |  |  | HG 2 Wire | [7 empty] | ME14S250 | 5/8 BV | SPT2 79
12 | 5,3 | 8Dr QIV5V14 |  |  | 1 | Frozen Food N49,N50 | 10.6 | -11 | HG 2 Wire | 1.68 | 115 | 1.2 | 7.68 | 193.2 | 138 | 883.2 | ME14S250 | 5/8 BV | SPT2 79 | 120 | 1 1/8 | 7/8 | 5/8
13 | 5,5,3 | 13Dr QIV5V14 |  |  | 1 | Ice Cream N46-N48 | 18.54 | -18 | HG 2 Wire | 2.73 | 115 | 2.1 | 12.65 | 313.95 | 241.5 | 1454.75 | ME14S250 | 5/8 BV | SPT2 1113 | 165 | 1 3/8 | 1 3/8 | 5/8
14 | 5,5,3 | 13Dr QIV5V14 |  |  | 1 | Ice Cream N43-N45 | 18.54 | -18 | HG 2 Wire | 2.73 | 115 | 2.1 | 12.65 | 313.95 | 241.5 | 1454.75 | ME14S250 | 5/8 BV | SPT2 911 | 185 | 1 3/8 | 1 3/8 | 5/8
15 | 12x35x8.5 | 2)AG36-120 |  | EXISTING | 1 | Storage Freezer | 25 | -15 | HG 2 Wire | 3 | 230/1 | 0 | 0 | 0 | 0 | 0 | ME14S250 | ME14S250 | SPT2 911 | 94 | 1 3/8 | 1 1/8 | 5/8
16 | 12'X15'X8.5 | ITG24-325 |  | NEW | 1 | Ice Cream Freezer | 13.65 | -18 | HG 2 Wire | 4.6 | 230/1 | 0 | 0 | 0 | 0 | 0 | ME14S250 | ME14S250 | SPT2 79 | 123 | 1 1/8 | 1 1/8 | 5/8
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | Existing |  |  | Compressor Specifications | [10 empty] | NEW | Condenser
Refrigerant Type |  |  | R407A | Compressor | Comp |  | Cap | Suct |  |  |  |  | Suction |  |  | Capacity | Circuit |  | Wire Size | Model # |  | RDD038
Condensing Temp |  |  | 110 | Group # | # | Compressor | MBTU | ° F | HP | RPM | RLA | LRA | Filter |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 9.7
Outside Air Temp. |  |  | 100 | 1 | 1 | 4DS3F76KE | 68.18 | -20 | 22 |  | 66 |  |  |  |  | UNLD | 90A | 75A | #3 | F P I |  | 10
Required MBTUH Group 1 |  |  | 243.31 | 1 | 2 | 4DS3F76KE | 68.18 | -20 | 22 |  | 66 |  |  |  |  | UNLD | 90A | 75A | #3 | Voltage |  | 208 / 3
Comp. Capac. MBTUH Group 1 |  |  | 221.54 | 1 | 3 | 4DT3F76KE | 68.18 | -20 | 22 |  | 66 |  |  |  |  | 0 | 90A | 75A | #3 | FLA |  | 24
Effective capac. with subcooling |  |  | 294.6482 | NEW | 4 | 2DL3R78KL-TFC-441 | 17 | -20 | 3.5 |  | 26.3 |  |  |  |  | 0 | 40A | 30A | #8 | MCA |  | 25.1
% Loaded Group 1 |  |  | 82.58% | [16 empty] | MOPD |  | 30
Rej. Heat (MBH) Group 1 |  |  | 369.9718 |  |  | CHANGE 4DT3-220L TO 2DL3R78KL-TFC-441 | [13 empty] | Weight |  | 2485
|  |  | 0 | [16 empty] | Size |  | 90.75X146"
Required MBTUH Group 2 |  |  | 0 | [16 empty] | # of Fans |  | 6
Comp. Capac. MBTUH Group 2 |  |  | 0 | [16 empty] | Line To |  | 2)1 3/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2)1 1/8
% Loaded Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5294 | FLOAT | Drain Regulator |  |  | -- |  |  | Air reclaim |  | 12D13B |  | Head Fan LT/MT |  | YES
|  |  | 0 |  | Oil Separator -- Group 2 |  | -- |  | Master Solenoid |  |  | -- |  |  | Water Reclaim |  | 12D13B |  | Crankcase Htrs. |  | NO
Required MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve - Grp 1 |  | MS-26 |  | Surge Solenoid |  |  | REMOVE |  |  | Line size To |  | 1 5/8
Comp. Capac. MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Group 2 |  | -- |  | Surge Ball Valve |  |  | 1 1/8 |  |  | Line size From |  | 1 5/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  | DDR-20 |  | Surge Check |  |  | -- |  |  | Bypass Valve |  | 10# (WATER) |  | Suction Crossover / Load Shed
% Loaded Group 3 |  |  |  |  | Bypass Regulator |  | -- |  | Surge Style |  |  | BYPASS |  |  | Split Cond. Valve |  | 12D13B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil type |  | MINERAL |  | Attron |  |  | -- |  |  | Receiver H / V |  | VERTICAL |  | Ball Valve
|  |  | 0 |  | Brand / Number |  | -- | [7 empty] | Dia. x Length |  | 16" X 60" |  | Check Valve
Total Rej. Heat (MBH) |  |  | 369.9718 |  | Reservoir Capacity |  | 2 GAL. |  | Subcooler |  |  | B10 X 30 |  |  | Lbs @ 90% PD |  | 390 |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 184.9859 |  | Suction Filter Main / Ind |  | (2)4CFA-42S |  | Liquid Temp Out |  |  | 50 F |  |  | PUMP OUT KIT |  | ADD |  | C P R
Compressor Capacity (Tons) |  |  | 18.4617 |  | Drier |  | C-969 |  | TEV |  |  | EBFVE-C-C | [6 empty] | From / To
Rack Size |  |  | 140x36x78
Estimated Rack Weight |  |  | 4200 |  |  | CONDENSER TO BE 50%/50% SPLIT DUAL HEADER