## Rack A
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Morganton, NC |  |  |  | Rack Model: | HUSSMANN MT1 | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2250 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY 10/31/19 |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/31/19 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | Danfoss
0 | [10 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
0 | 0 | 0 | 0 | [7 empty] | MCA |  |  |  | 312 |  |  | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 350
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
11 | 17X33 | (2)GAH26130A |  | EXISTING |  | Meat Prep | 38.6 | 30 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
22 | [5 empty] | SPARE |  |  | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
7 | 36' | D5E |  |  |  | Lunch Meat 35-37 | 48.8 | 24 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
5 | 28' | D5E/D5LRE |  |  |  | Dairy 46-48 | 42.8 | 24 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
6 | 17X30 | MK26290A |  | EXISTING |  | Diary Cooler | 29.1 | 26 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
4 | 44' | D5LE |  |  |  | Dairy 49-52 | 62.7 | 24 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 15 |  | 1 3/8 |  | 5/8
3 | 32' | D5LE |  |  |  | Dairy 53-55 | 45.6 | 24 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
2 | 28' | D5LE |  |  |  | Beer 56-58 | 39.9 | 24 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
1 | 28' | D5LE |  |  |  | Beer 59-61 | 39.9 | 24 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
SC |  | Subcooler |  |  |  | LT Subcooler | 79 | 40 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | ORIT 20 |  | 1 5/8 |  | 5/8
SP | [5 empty] | SPARE | [7 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | HUSSMANN MT1 |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | LCVT10408K
Condensing Temp |  |  | 110 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 13.1
Outside Air Temp. |  |  | 100 | 1 | 1 | 2DL3-0750-TFC-423 | 57.2 | 22 | 7.5 |  | 31.6 |  | 2DL3-0750-TFC-423 |  |  | 0 | 40A | 40A | #8 | F P I |  | 8
Required Load Group 1 |  |  | 465.2 | 1 | 2 | 3DB3A-100L-TFC-423 | 94.4 | 22 | 10 |  | 43.6 |  | 3DB3A-100L-TFC-423 |  |  | 0 | 60A | 50A | #6 | Voltage |  | 208/3
Comp. Capacity Group 1 |  |  | 520.5 | 1 | 3 | 3DF3A-120L-TFC-423 | 109.9 | 22 | 12 |  | 48.2 |  | 3DF3A-120L-TFC-423 |  |  | 0 | 70A | 50A | #4 | FLA |  | 34
Effective capac. with subcooling |  |  | 520.5 | 1 | 4 | 3DS3A-150L-TFC-423 | 125.1 | 22 | 15 |  | 59.6 |  | 3DS3A-150L-TFC-423 |  |  | 0 | 80A | 60A | #4 | MCA |  | 36
% Excess Capacity Group 1 |  |  | 11.89% | 1 | 5 | 4DA3-200L-TSK-423 | 133.9 | 22 | 20 |  | 66 |  | 4DA3-200L-TSK-423 |  |  | 0 | 90A | 75A | #3 | MOPD |  | 40
Rej. Heat (MBH) Group 1 |  |  | 707.88 | [16 empty] | Weight |  | 4780
|  |  | 0 | [16 empty] | Size |  | 96X274
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans |  | 10
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2)2 1/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2)1 5/8
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5608 |  | Drain Regulator |  |  | A81 |  |  | Air reclaim |  | 16D17B |  | Head Fan LT/MT |  | YES
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  | 16D17B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  | SF283F |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  | VERTICAL |  | Check Valve
Total Rej. Heat (MBH) |  |  | 707.88 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  | 20 X 63 |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 353.94 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 43.4 |  | Drier |  | C14413GR |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight Lbs. | [13 empty] | *Condenser MCA included in Rack

## Rack B
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack B | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Morganton, NC |  |  |  | Rack Model: | HUSSMANN MT2 | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2250 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY 10/31/19 |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/31/19 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | Danfoss
0 | 0 | 0 | 0 | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
0 | 0 | 0 | 0 | [7 empty] | MCA |  |  |  | 290 |  |  | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 350
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
30 | 40' | M1GE |  |  |  | SD Meat 28-31 | 16.6 | 18 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
29 | 8' | C2LGE |  |  |  | Seafood 27 | 7.6 | 21 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
28 | 14X22 | GAH26130A |  | EXISTING |  | Seafood Prep | 20 | 30 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
27 | 7X11 | HC6A090AB |  | EXISTING |  | Seafood Cooler | 8.4 | 20 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
26 | 16X24 | HC6A278BB |  | EXISTING |  | Produce Cooler | 26.1 | 26 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
25 | 17X28 | GAH46270A |  | EXISTING |  | Produce Prep | 35.1 | 30 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
24 | 16 | C5 |  |  |  | SD Produce 13,14 | 8.3 | 18 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
21 | 2) 12' | (2) PW/PWE |  |  |  | Produce Tables 15-22 | 41 | 21 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
23 | 24' | D5LE |  |  |  | MD Produce 11,12 | 34.2 | 24 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
8 | 36' | M4GE |  |  |  | MD Meat 32-34 | 41.8 | 21 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
20 | 40' | P2E |  |  |  | Produce 7-10 | 38.8 | 24 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
19 | 12' | PT/PTD |  |  |  | Bakery 2 | 13.7 | 18 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
14 | 12' | BMD |  |  |  | Service Deli 1 | 10.4 | 18 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 1/2
15 | [5 empty] | SPARE |  |  | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
13 | 7X10 | HC6A076BB |  | EXISTING |  | Deli Cooler | 7.4 | 20 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 1/2
18 | 10' | PFI |  |  |  | Cheese island 4,5 | 24.35 | 18 | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 20 |  | 1 3/8 |  | 5/8
12 | [5 empty] | SPARE |  |  | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
17 | 6' | NFT-3 |  |  | 0 | Floral Combo | 6.9 | 22 | Off Cycle | 1.88 | 115 | 2.35 | 0 | 216.2 | 270.25 | 0 |  |  | SORIT 12 |  | 7/8 |  | 1/2
16 | [5 empty] | SPARE |  |  | Off Cycle |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12
SP | [5 empty] | SPARE | [7 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | HUSSMANN MT2 |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | LCVR8408K
Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 13.7
Outside Air Temp. |  |  | 100 | 1 | 1 | 2DD3-050L-TSK-423 | 38.65 | 16 | 5 |  | 22.3 |  |  |  |  | 0 | 30A | 25A | #10 | F P I |  | 8
Required Load Group 1 |  |  | 340.65 | 1 | 2 | 3DB3A-100L-TFC-423 | 82.7 | 16 | 10 |  | 43.6 |  |  |  |  | 0 | 60A | 50A | #6 | Voltage |  | 208/3
Comp. Capacity Group 1 |  |  | 419.15 | 1 | 3 | 4DH3-250L-TSK-423 | 148.9 | 16 | 25 |  | 82.2 |  |  |  |  | 0 | 125A | 90A | #1 | FLA |  | 27.2
Effective capac. with subcooling |  |  | 419.15 | 1 | 4 | 4DH3-250L-TSK-423 | 148.9 | 16 | 25 |  | 82.2 |  |  |  |  | 0 | 125A | 90A | #1 | MCA |  | 30
% Excess Capacity Group 1 |  |  | 18.73% | [16 empty] | MOPD |  | 35
Rej. Heat (MBH) Group 1 |  |  | 578.427 | [16 empty] | Weight |  | 2910
|  |  | 0 | [16 empty] | Size |  | 96 X 220
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans |  | 8
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2)2 1/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2)1 5/8
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5608 |  | Drain Regulator | [5 empty] | Air reclaim |  | 16D17B |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 2 1/8
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 2 1/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  | 16D17B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  | SF283F |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  | VERTICAL |  | Check Valve
Total Rej. Heat (MBH) |  |  | 578.427 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  | 20 X 63 |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 289.2135 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  | 607 |  | C P R
Compressor Capacity (Tons) |  |  | 34.9 |  | Drier |  | C-14413GR |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight Lbs. | [12 empty] | *Condenser MCA included in Rack

## Rack C Pg 1
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack C | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Morganton, NC |  |  |  | Rack Model: | 0 | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2250 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY 10/31/19 |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/31/19 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | Danfoss
[11 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
[11 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
[11 empty] | MCA | [6 empty] | Fixture Plan:
Max. Overcurrent
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
36 | 8' | M1L |  |  | 1 | Single Deck Seafood 26 | 4.2 | -20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
35 | 5 Drs | RL |  |  | 1 | Frozen Seafood 25 | 6.5 | -11 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
34 | 6' | LN |  |  | 1 | Dual Temp Seafood 24 | 2.3 | -20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
33 | 6' | LN |  |  | 1 | Dual Temp Seafood 23 | 2.3 | -20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
32 | 12' | NF6 |  |  | 1 | Frozen Cake 3 | 15.5 | -13 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
31 | 8x16 | HC4P133BA |  | EXISTING | 1 | Bakery Freezer | 11.4 | -15 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
41 | 6 Drs | RL |  |  | 1 | Frozen Meat 38,39 | 7.8 | -11 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 1/8 |  | 5/8
39 | 8' | LN |  |  | 1 | Dual Temp Meat 43 | 3.1 | -20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
37 | 8' | LN |  |  | 1 | Dual Temp Meat 41 | 3.1 | -20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
40 | 8' | LN |  |  | 1 | Dual Temp Meat 42 | 3.1 | -20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
38 | 8' | LN |  |  | 1 | Dual Temp Meat 40 | 3.1 | -20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
42 | 17x28 | 2)MK24210KGE |  | EXISTING | 1 | Storage Freezer | 33.6 | -25 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 20 |  | 1 5/8 |  | 5/8
47 | 15 Drs | RL |  |  | 1 | Frozen Food / IC 80-83 | 20.6 | -19 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
50 | 17 Drs | RL |  |  | 1 | Frozen Food / IC 76-79 | 23.3 | -19 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
51 | 15 Drs | RL |  |  | 1 | Ice Cream 63-65 | 20.6 | -19 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
44 | 6' | LN |  |  | 1 | Dual Temp Dairy 45 | 2.3 | -20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
45 | 6' | LN |  |  | 1 | Dual Temp Dairy 44 | 2.3 | -20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
46 | 16 Drs | RL |  |  | 1 | Frozen Food / IC 69-72 | 21.9 | -19 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  |  | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model #
Condensing Temp |  |  |  | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D.
Outside Air Temp. | [19 empty] | F P I
Required Load Group 1 |  |  | 0 | [16 empty] | Voltage
Comp. Capacity Group 1 |  |  | 0 | [16 empty] | FLA
Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA
% Excess Capacity Group 1 | [19 empty] | MOPD
Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight
|  |  | 0 | [16 empty] | Size
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 0 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight Lbs.

## Rack C Pg 2
Kysor Warren Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | RACK C | [13 empty] | Kysor Warren Cases
5 Corporate Ridge Pkwy |  |  |  | Location: | Morganton, NC |  |  |  | Rack Model: | HUSSMANN LT1 | [12 empty] | 5201 Transport Blvd.
Columbus, GA 31907 |  |  |  | Store #: | 2250 |  |  |  | Salesman | Kim Austin | [12 empty] | Columbus, GA 31907
800-866-5596 |  |  |  | Job #: | EXISTING SUMMARY 10/31/19 |  |  |  | Prepared By: | Kim Austin |  | Date Originated |  |  | 10/31/19 | [7 empty] | 800-866-5596
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | Danfoss
0 | [10 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
0 | 0 | 0 | 0 | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
0 | 0 | 0 | 0 | [7 empty] | MCA |  |  |  | 318 |  |  | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 350
Kysor Warren assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
48 | 13 Drs | RL |  |  |  | Ice Cream 66-68 | 17.8 | -19 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 3/8 |  | 5/8
49 | 18 Drs | RL |  |  |  | FF/ Ice Cream 62,73-75 | 24.7 | -19 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 1 5/8 |  | 5/8
10 | 18x28 | HC6P140BA |  | EXISTING |  | 1/2 Meat Cooler | 15.2 | 20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
9 | 18x28 | HC6P140BA |  | EXISTING |  | 1/2 Meat Cooler | 15.2 | 20 | Kool Gas |  |  |  |  | 0 | 0 | 0 |  |  | SORIT 12 |  | 7/8 |  | 5/8
SP | [13 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | HUSSMANN LT1 |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-507 | Compressor | Comp |  |  | Suct | [7 empty] | Capacity | Circuit |  | Wire Size | Model # |  | LCVR8410K
Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Suction Filter |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 9.6
Outside Air Temp. |  |  | 100 | 1 | 1 | 2DB3-06L-TFC-423 | 21.8 | -28 | 6 |  | 28.2 |  | 4811SV - F48 |  |  | 0 | 40A | 30A | #8 | F P I |  | 10
Required Load Group 1 |  |  | 259.9 | 1 | 2 | 4DA3-101L-TSK-423 | 42.2 | -28 | 10 |  | 45.2 |  | 4813SV - F48 |  |  | 0 | 60A | 50A | #6 | Voltage |  | 208/3
Comp. Capacity Group 1 |  |  | 246.3 | 1 | 3 | 4DL3-150L-TSK-423 | 57.4 | -28 | 15 |  | 52.6 |  | 4813SV - F48 |  |  | 0 | 70A | 60A | #4 | FLA |  | 27.2
Effective capac. with subcooling |  |  | 300.486 | 1 | 4 | 4DL3-150L-TSK-423 | 57.4 | -28 | 15 |  | 52.6 |  | 4813SV - F48 |  |  | 0 | 70A | 60A | #4 | MCA |  | 30
% Excess Capacity Group 1 |  |  | 15.62% | 1 | 5 | 4DT3-220L-TSK-423 | 67.5 | -28 | 22 |  | 66 |  | 4817SV- F48 |  |  | 0 | 90A | 75A | #3 | MOPD |  | 35
Rej. Heat (MBH) Group 1 |  |  | 418.71 | [16 empty] | Weight |  | 3040
|  |  | 0 | [16 empty] | Size |  | 96X230"
Required Load Group 2 |  |  | 0 |  |  |  |  | 0 | [11 empty] | # of Fans |  | 8
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To |  | 2) 1 5/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2) 1 3/8
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5604 |  | Drain Regulator |  |  | A81 |  |  | Air reclaim |  | 12D13B |  | Head Fan LT/MT |  | NO
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs. |  | NO
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 1 5/8
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 1 5/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  | OLDR-15 |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  | 12D13B-SC |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  | OF-303 |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  | Vertical |  | Check Valve
Total Rej. Heat (MBH) |  |  | 418.71 |  | Suction Filter -- Group 1 |  |  |  | Subcooler |  |  | CB26-34H |  |  | Dia. x Length |  | 20 X 63 |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 209.355 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  | 528 |  | C P R
Compressor Capacity (Tons) |  |  | 20.5 |  | Drier |  | C-9611GR |  | TEV | [9 empty] | From / To
Rack Size |  |  | 208X39X79
Estimated Rack Weight Lbs. |  |  | 6270 | [10 empty] | *Condenser MCA included in Rack