## Remodel Rack A (Part 1)
Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | [13 empty] | Display Systems
709 Sigman Road |  |  |  | Location: | ESSEX, MD |  |  |  | Rack Model: | Existing | [12 empty] | 1925 Ruffin Mill Road
Conyers, Georgia 30013 |  |  |  | Store #: | 1653 |  |  | Salesman |  | Kim Austin | [12 empty] | Colonial Heights, VA 23834
(770) 388-0706, Fax:(770) 285-3074 |  |  |  | Job #: | 119439 |  |  | Prepared By: |  | Sandy Yon |  | Date Originated |  |  | 01/19/05 | [7 empty] | (804) 526-4455, Fax: (804) 526-2804
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
| 9/29/19 | J.Finch | Revised to Store Survey. | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
[11 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer |  |  |  | Kysor
[11 empty] | MCA | [6 empty] | A-12 Date:
Max. Overcurrent
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | MBTU | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
1 | 24 | L4M |  |  | 0 | Multi Deck Fresh Meat 32,33 | 33.1 | 15 | Hot Gas | 3.6 | 120 | 1.8 | 1 | 432 | 216 | 120 | 0 | 0 | SPRT2-1111 | 13 | 1 1/8 | 1.125 | 0.625
2 | 12 | L4M |  |  | 0 | Multi Deck Fresh Meat 31 | 16.55 | 15 | Hot Gas | 1.8 | 120 | 0.9 | 0.5 | 216 | 108 | 60 | 0 | 0 | SPRT2 09-09 | 20 | 0.875 | 0.875 | 0.625
3 | 32 | L4M |  |  | 0 | Fresh Meat + 2 Wedges 35-30 | 16.768 | 15 | Hot Gas | 4 | 120 | 0 | 1.1 | 480 | 0 | 132 | 0 | 0 | SPRT2 09-09 | 45 | 0.875 | 0.875 | 0.625
4 | 24'X34'X9 | 2)FL36-100 |  |  | 0 | Meat Prep Closed Area | 40.8 | 35 | Off Cycle | 3.6 | 115 | 0 | 0 | 432 | 0 | 0 | 0 | 0 | SPRT2 11-11 | 50 | 1 1/8 | 1.125 | 0.5
5 | 15'X24'X9' | AG46-164 |  |  | 0 | Meat Cooler | 21.319 | 20 | Hot Gas | 2 | 208 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | SPRT2 09-09 | 80 | 0.875 | 0.875 | 0.625
6 | 16'X24'X9' | AA38-195 |  |  | 0 | Produce Cooler | 16.07 | 25 | Off Cycle | 6 | 208 | 0 | 0 | 1380 | 0 | 0 | 0 | 0 | SPRT2 09-09 | 85 | 0.875 | 0.875 | 0.375
7 | 22'X33'X9' | 2)FL26-67A |  |  | 0 | Produce Prep | 36.3 | 35 | Off Cycle | 2.4 | 115 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | SPRT2 11-11 | 120 | 1 1/8 | 0.875 | 0.5
8 | 12' | L6DMA |  |  |  | MD Deli Meat 21 | 15 | 20 | Off Cycle | 0.8 | 115 | 4.8 |  | 96 | 576 | 0 | 0 | 0 | SPT2 09-09 | 175 | 1 1/8 | 7/8 | 1/2
9 | 8' | D61 |  |  | 0 | Produce 18 | 11.6 | 20 | Off Cycle | 0.64 | 115 | 0.92 |  | 69 | 106 | 0 | 0 | 0 | SPRT2 09-09 | 118 | 1.375 | 1 5/8 | 5/8
10 | 8'8'12'12' | 40' D6L1 |  |  | 0 | Produce 14-17 | 58 | 20 | Off Cycle | 3.2 | 115 | 4.8 | 0 | 368 | 552 | 0 | 0 | 0 | SPRT2 09-09 | 180 | 7/8 | 7/8 | 1/2
11 | 8'12' | 20' HZVP1 |  |  | 0 | Produce 12,13 | 21 | 20 | Off Cycle | 0.96 | 115 | 2.4 | 0 | 111 | 281 | 0 | 0 | 0 | SPRT2 11-11 | 270 | 1 1/8 | 7/8 | 1/2
12 | 6' | NFT-3 |  |  | 0 | Floral Combo | 6.9 | 22 | Off Cycle | 1.62 | 115 | 2.01 | 0 | 186 | 230 | 0 | 0 | 0 | SPRT2 07-07 | 370 | 7/8 | 5/8 | 1/2
13 | 24 | L6DMA |  |  | 0 | MD Deli Meat 19,20 | 34.608 | 21 | Off Cycle | 3.6 | 115 | 4.2 | 0 | 432 | 504 | 0 | 0 | 0 | SPRT2 11-11 | 120 | 1 1/8 | 1 1/8 | 1/2
14 | 8'8'8' | 16' LSSD/8' PFI |  |  | 0 | Deli/Cheese Promo | 34.9 | 20 | Off Cycle | 4.5 | 115 | 6.02 | 0 | 540 | 722.4 | 0 | 0 | 0 | SPRT2 09-09 | 245 | 1 3/8 | 1 1/8 | 1/2
15 | 16 | LSSD |  |  | 0 | Bakery | 15.42 | 15 | Off Cycle | 2 | 115 | 1 |  | 240 | 120 | 0 | 0 | 0 | SPRT2 05-07 | 245 | 1 1/8 | 7/8 | 1/2
16 | 7'X14'X9' | AA28-097 |  |  | 0 | Deli Cooler | 7.412 | 20 | Off Cycle | 4 | 115 | 0 | 0 | 480 | 0 | 0 | 0 | 0 | SPRT2 05-09 | 235 | 0.875 | 0.625 | 0.375
17 | 8'12' | 20' L4MG |  |  |  | Self-Serve Cold Deli | 32.58 | 15 | Off Cycle | 3 | 115 | 1.5 | 0.8 | 360 | 180 | 96 | 0 | 0 | SPRT2 11-11 | 175 | 1 3/8 | 1.125 | 0.625
18 |  |  |  |  | 0 | Future MD Beer | [9 empty] | 0 | 0 | 0 | SPRT2 11-11 | 175 | 1 5/8 | 1.375 | 0.625
19 | 24' | L6DLA | Retrofit Doors |  | 0 | Multi Deck Dairy44,45 | 14 | 30 | Off Cycle | 1.8 | 115 | 12.6 | 0 | 216 | 1512 | 0 | 0 | 0 | SPRT2 11-11 | 190 | 1 1/8 | 1 1/8 | 1/2
| 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  |  | Compressor | Comp |  | Cap | Suct |  |  |  |  | Suction |  |  | Capacity | Circuit |  | Wire Size | Model #
Condensing Temp |  |  |  | Group # | # | Compressor | MBTU | ° F | HP | RPM | RLA | LRA | Filter |  |  | Control | Breaker | Contactor | (AWG) | T.D.
Outside Air Temp. | [19 empty] | F P I
Required MBTUH Group 1 |  |  | 0 | [16 empty] | Voltage
Comp. Capac. MBTUH Group 1 |  |  | 0 | [16 empty] | FLA
Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA
% Loaded Group 1 | [19 empty] | MOPD
Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight
|  |  | 0 | [16 empty] | Size
Required MBTUH Group 2 |  |  | 0 | [16 empty] | # of Fans
Comp. Capac. MBTUH Group 2 |  |  | 0 | [16 empty] | Line To
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From
% Loaded Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
Comp. Capac. MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Loaded Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil type |  |  |  | Attron | [5 empty] | Receiver H / V |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Dia. x Length |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 0 |  | Reservoir Capacity |  |  |  | Subcooler | [5 empty] | Lbs @ 90% PD |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter (Group) |  |  |  | Liquid Temp Out | [9 empty] | C P R
Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size
Estimated Rack Weight

## Remodel Rack A (Part 2)
Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | [13 empty] | Display Systems
709 Sigman Road |  |  |  | Location: | ESSEX, MD |  |  |  | Rack Model: | Existing | [12 empty] | 1925 Ruffin Mill Road
Conyers, Georgia 30013 |  |  |  | Store #: | 1653 |  |  | Salesman |  | Kim Austin | [12 empty] | Colonial Heights, VA 23834
(770) 285-3100, Fax:(770) 285-3076 |  |  |  | Job #: | 119439 |  |  | Prepared By: |  | Sandy Yon |  | Date Originated |  |  | 01/19/05 | [7 empty] | (804) 526-4455, Fax: (804) 526-2804
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
| 9/29/19 | J.Finch | Revised to Store Survey. | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
[11 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer |  |  |  | Kysor
[11 empty] | MCA |  |  |  | 439.775 |  |  | A-12 Date:
[11 empty] | Max. Overcurrent |  |  |  | 500
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | MBTUH | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
20 | 36 | L6DLA | Retrofit Doors |  |  | Multi Deck Dairy 41-43 | 18 | 30 | TO | 5.4 | 115 | 6.3 |  | 648 | 756 | 0 | 0 | 0 | SPRT2 11-11 | 125 | 1 1/8 | 1.375 | 0.625
21 | 12 | L6DMA | Retrofit Doors |  |  | Multi Deck Dairy 39,40 | 6 | 30 | TO | 1.8 | 115 | 2.1 | 0 | 216 | 252 | 0 | 0 | 0 | SPRT2 09-09 | 90 | 0.875 | 0.875 | 0.625
22 | [5 empty] | Spare | [9 empty] | 0 | 0 | 0 | SPRT2 09-09 | 80 | 0.875 | 0.875 | 0.375
23 | 16 | L6DLA | Retrofit Doors |  |  | Multi Deck Dairy 37,38 | 8 | 30 | TO | 2.4 | 115 | 2.6 | 0 | 288 | 312 | 0 | 0 | 0 | SPRT2 09-09 | 65 | 1 1/8 | 0.875 | 0.375
24 | 13'X36'X09' | 2)AA28-122 |  |  |  | Dairy Cooler | 23.344 | 20 | TO | 4 | 115 | 0 | 0 | 480 | 0 | 0 | 0 | 0 | SPRT2 09-09 | 85 | 1.125 | 0.875 | 0.375
25 | 8' | 8'BCHV1-508 |  |  |  | Seafood Island 23 | 16.1 | 18 | Off Cycle | 3.3 | 115 | 3.92 | 0 | 380 | 449 | 0 | 0 | 0 | SPRT2 07-07 | 80 | 7/8 | 7/8 | 1/2
26 | 0 | 0 |  |  |  | Subcooling | 67.458 | 35 | TO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PORT2 11-11 | 20 | 1 1/8 |  | 0.5
[16 empty] | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | Existing |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  | Cap | Suct |  |  |  |  | Suction |  |  | Capacity | Circuit |  | Wire Size | Model # |  | VEQ 149
Condensing Temp |  |  | 115 | Group # | # | Compressor | MBTU | ° F | HP | RPM | RLA | LRA | Filter |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 16.197
Outside Air Temp. |  |  | 100 |  | 1 | 06DM337 | 96.18 | 15 | 10 |  | 44.3 | [8 empty] | F P I
Required MBTUH Group 1 |  |  | 571.229 |  | 2 | 06EA565 | 164.423 | 15 | 25 |  | 90.7 | [5 empty] | 125A | 0 | #1 | Voltage |  | 208/3
Comp. Capac. MBTUH Group 1 |  |  | 787.79 |  | 3 | 06EA565 | 164.423 | 15 | 25 |  | 90.7 | [5 empty] | 125A | 0 | #1 | FLA
Effective capac. with subcooling |  |  | 787.79 |  | 4 | 06EM475 | 181.364 | 15 | 25.5 |  | 90.7 | [5 empty] | 125A | 0 | #1 | MCA |  | 54.3
% Loaded Group 1 |  |  | 72.51% |  | 5 | 06EM475 | 181.4 | 15 | 25.5 |  | 90.7 | [5 empty] | 125A | 0 | #1 | MOPD |  | 60
Rej. Heat (MBH) Group 1 |  |  | 1197.4408 | [16 empty] | Weight |  | 2950
|  |  | 0 | [16 empty] | Size |  | 242X96X43
Required MBTUH Group 2 |  |  | 0 |  |  |  |  | 0 | [11 empty] | # of Fans |  | 2x5
Comp. Capac. MBTUH Group 2 |  |  | 0 | [16 empty] | Line To |  | 2) 2 1/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2) 1 5/8
% Loaded Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5202 |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT |  | NO
|  |  | 0 |  | Oil Separator -- Group 2 |  | S-5202 |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs. |  | NO
Required MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 2 1/8
Comp. Capac. MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 2 1/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  | DDR-20 |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Loaded Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil type |  |  |  | Attron | [5 empty] | Receiver H / V |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Dia. x Length |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 1197.4408 |  | Reservoir Capacity |  |  |  | Subcooler | [5 empty] | Lbs @ 90% PD |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 598.7204 |  | Suction Filter (Group) |  |  |  | Liquid Temp Out |  |  | -- | [6 empty] | C P R
Compressor Capacity (Tons) |  |  | 65.6 |  | Drier |  |  |  | TEV |  |  | -- | [6 empty] | From / To
Rack Size |  |  | 192X38X80
Estimated Rack Weight |  |  | 2950

## Remodel Rack B (Part 3)
Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack B | [13 empty] | Display Systems
709 Sigman Road |  |  |  | Location: | ESSEX, MD |  |  |  | Rack Model: | Existing | [12 empty] | 1925 Ruffin Mill Road
Conyers, Georgia 30013 |  |  |  | Store #: | 1653 |  |  | Salesman |  | Kim Austin | [12 empty] | Colonial Heights, VA 23834
(770) 285-3100, Fax:(770) 285-3076 |  |  |  | Job #: | 119439 |  |  | Prepared By: |  | Sandy Yon |  | Date Originated |  |  | 01/19/05 | [7 empty] | (804) 526-4455, Fax: (804) 526-2804
Rev. | Date | By: |  |  | Revision: | [5 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
| 9/29/19 | J.Finch | Revised to Store Survey. | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
[11 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer |  |  |  | Kysor
[11 empty] | MCA |  |  |  | 363.4 |  |  | A-12 Date:
[11 empty] | Max. Overcurrent |  |  |  | 450
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | MBTUH | ° F | Type | Amps | Volts/Ø | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
1 | 10X11X09 | AG36-120 |  |  | 0 | Meat Freezer | 10.344 | -25 | HG | 3 | 208 | 0 | 0 | 690 | 0 | 0 | 0 | 0 | SPRT2 07-07 | 85 | 1 1/8 | 0.625 | 0.625
2 | 3 Door | L5FGA |  |  | 0 | Reach-in Frozen Deli 11 | 4.614 | -16 | HG | 2.2 | 115 | 4.2 | 2.1 | 264 | 504 | 252 | 0 | 0 | SPRT2 05-07 | 150 | 5/8 | 1/2 | 5/8
3 | 12X18X09 | AG46-164 |  |  | 0 | Bakery Freezer | 15.381 | -25 | HG | 4 | 208 | 0 | 0 | 920 | 0 | 0 | 0 | 0 | SPRT2 09-09 | 255 | 1.375 | 0.875 | 0.625
4 | 8 | LFW |  |  | 0 | Meat Promo Dual Temp 24 | 3.6 | -25 | HG | 1 | 115 | 1.8 | 0 | 120 | 216 | 0 | 0 | 0 | SPRT2 05-07 | 40 | 1 1/8 | 0.5 | 0.625
5 | 14 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 34-36 | 21.532 | -16 | HG | 9.8 | 115 | 19.1 | 9 | 1176 | 2292 | 1080 | 0 | 0 | SPRT2 11-11 | 40 | 1.125 | 0.875 | 0.625
6 | 10 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 61,62 | 15.38 | -16 | HG | 7 | 115 | 13.6 | 6.4 | 840 | 1632 | 768 | 0 | 0 | SPRT2 09-09 | 110 | 1.125 | 0.875 | 0.625
7 | 10 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 63,64 | 15.38 | -16 | HG | 7 | 115 | 13.6 | 6.4 | 840 | 1632 | 768 | 0 | 0 | SPRT2 09-09 | 85 | 1.125 | 0.875 | 0.625
8 | 13 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 65-67 | 19.994 | -16 | HG | 9.2 | 115 | 17.8 | 8.5 | 1104 | 2136 | 1020 | 0 | 0 | SPRT2 09-09 | 70 | 1.125 | 0.875 | 0.625
9 | 15 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 58-60 | 23.07 | -16 | HG | 10.5 | 115 | 20.4 | 9.6 | 1260 | 2448 | 1152 | 0 | 0 | SPRT2 11-11 | 125 | 1.375 | 1.125 | 0.625
10 | 10 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 56,57 | 15.38 | -16 | HG | 7 | 115 | 13.6 | 6.4 | 840 | 1632 | 768 | 0 | 0 | SPRT2 09-09 | 90 | 1.125 | 0.875 | 0.625
11 | 14 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 52-55 | 21.532 | -16 | HG | 9.8 | 115 | 19.1 | 9 | 1176 | 2292 | 1080 | 0 | 0 | SPRT2 11-11 | 80 | 1.125 | 0.875 | 0.625
12 | 14 Door | L5FGA |  |  | 0 | Reach-in Ice Cream 49-51 | 23.184 | -23 | HG | 9.8 | 115 | 19.1 | 9 | 1176 | 2292 | 1080 | 0 | 0 | SPRT2 11-11 | 110 | 1.375 | 1.125 | 0.625
13 | 13 Door | L5FGA |  |  | 0 | Reach-in Ice Cream 46-48 | 21.528 | -23 | HG | 9.2 | 115 | 17.8 | 8.5 | 1104 | 2136 | 1020 | 0 | 0 | SPRT2 11-11 | 130 | 1.375 | 1.125 | 0.625
14 | 12X35X09 | 2)AG36-140 |  |  | 0 | Grocery Freezer | 23.475 | -25 | HG | 6 | 208 | 0 | 0 | 1380 | 0 | 0 | 0 | 0 | SPRT2 11-11 | 110 | 1.375 | 1.125 | 0.625
15 | 12X15X09 | AG54-180 |  |  | 0 | Ice Cream Freezer | 13.867 | -25 | HG | 5 | 208 | 0 | 0 | 1150 | 0 | 0 | 0 | 0 | SPRT2 09-09 | 80 | 1.125 | 0.875 | 0.625
16 | 8' | IL1 |  |  | 1 | Meat Promo Dual Temp 22 | 3.2 | -20 | HG 2 Wire | 1.7 | 115 | 0 | 2 | 204 | 0 | 240 |  | 0 | SPRT2 05-07 | 110 | 5/8 | 1/2 | 5/8
0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  | Existing |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  | Cap | Suct |  |  |  |  | Suction |  |  | Capacity | Circuit |  | Wire Size | Model # |  | VEQ 91
Condensing Temp |  |  | 110 | Group # | # | Compressor | MBTU | ° F | HP | RPM | RLA | LRA | Filter |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 10
Outside Air Temp. |  |  | 100 |  | 1 | 06ER450 | 41.205 | -25 | 15 |  | 59.3 | [5 empty] | 80A | 60A | #4 | F P I |  | #VALUE!
Required MBTUH Group 1 |  |  | 251.461 |  | 2 | 06ER465 | 52.245 | -25 | 20 |  | 74.3 | [5 empty] | 100A | 75A | #3 | Voltage |  | 208/3
Comp. Capac. MBTUH Group 1 |  |  | 241.341 |  | 3 | 06ER475 | 65.759 | -25 | 20.5 |  | 74.3 | [5 empty] | 100A | 75A | #3 | FLA
Effective capac. with subcooling |  |  | 299.2628 |  | 4 | 06ER399 | 82.132 | -25 | 30 |  | 116.4 | [5 empty] | 125A | 0 | #1 | MCA |  | 33.1
% Loaded Group 1 |  |  | 84.03% | [16 empty] | MOPD |  | 35
Rej. Heat (MBH) Group 1 |  |  | 371.6651 | [16 empty] | Weight |  | 2050
|  |  | 0 | [16 empty] | Size |  | 147x96
Required MBTUH Group 2 |  |  | 0 | [16 empty] | # of Fans
Comp. Capac. MBTUH Group 2 |  |  | 0 | [16 empty] | Line To |  | 2) 1 5/8
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From |  | 2)1 1/8
% Loaded Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  | S-5292 |  | Drain Regulator |  |  | -- |  |  | Air reclaim |  |  |  | Head Fan LT/MT |  | YES
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs. |  | NO
Required MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To |  | 1 5/8
Comp. Capac. MBTUH Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From |  | 1 5/8
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  | DDR-20 |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Loaded Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil type |  |  |  | Attron | [5 empty] | Receiver H / V |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Dia. x Length |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 371.6651 |  | Reservoir Capacity |  |  |  | Subcooler | [5 empty] | Lbs @ 90% PD |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 185.8326 |  | Suction Filter (Group) |  |  |  | Liquid Temp Out | [9 empty] | C P R
Compressor Capacity (Tons) |  |  | 20.1 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size |  |  | 149X38X80
Estimated Rack Weight