## Remodel Rack A (Part 1)
Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | Existing | [12 empty] | Display Systems
2016 Gees Mill Road |  |  |  | Location: | ESSEX, MD |  |  |  | Rack Model: | [13 empty] | 1925 Ruffin Mill Road
Conyers, Georgia 30013 |  |  |  | Store #: | 1653 |  |  | Salesman |  | Kim Austin | [12 empty] | Colonial Heights, VA 23834
(770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: | 119439 |  |  | Prepared By: |  | Sandy Yon |  | Date Originated |  |  | 01/19/05 | [7 empty] | (804) 526-4455, Fax: (804) 526-1926
Rev. | Date | By: | Revision: | [7 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
A | 9/30/19 | J.Finch | Revised to new A1.01 Drawing. | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
A | 10/28/19 | DAB | Revised to new A1.01 Drawing. | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
[11 empty] | MCA | [6 empty] | Fixture Plan:
Max. Overcurrent
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
1 | 12'12'12' | L6DMA |  |  | 0 | MD Deli Meat 19,20, 21 | 49.6 | 20 | Off Cycle | 4.4 | 115 | 9 | 0 | 528 | 1080 | 0 |  |  | SPRT2-1111 | 20 | 1 3/8 | 1 3/8 | 5/8
2 | [5 empty] | Spare | [9 empty] | 0 |  |  | SPRT2 09-09
3 | 8'8'8'8' | 32' LSB |  |  | 1 | Six Deck Meat 16-19 | 46.24 | 29 | Off Cycle | 5.52 | 120 | 4.72 | 0 | 662.4 | 566.4 | 0 | 0 | 0 | SPRT2 09-09 | 65 | 1 3/8 | 1 1/8 | 1/2
4 | 24'X34'X9 | 2)RWF130 |  | New | 0 | Meat Prep Closed Area | 40.8 | 30 | Off Cycle | 2.4 | 115 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | SPRT2 11-11 | 50 | 1 1/8 | 1.125 | 0.5
5 | 15'X24'X9' | AG46-164 |  |  | 0 | Meat Cooler | 21.319 | 20 | Hot Gas | 2 | 208 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | SPRT2 09-09 | 80 | 0.875 | 0.875 | 0.625
6 | 16'X24'X9' | AA48-212 |  | New | 0 | Produce Cooler | 16.07 | 30 | Off Cycle | 4 | 115 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | SPRT2 09-09 | 85 | 0.875 | 0.875 | 0.375
7 | 22'X33'X9' | 2)FL26-67A |  |  | 0 | Produce Prep | 36.3 | 35 | Off Cycle | 2.4 | 115 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | SPRT2 11-11 | 120 | 1 1/8 | 0.875 | 0.5
8 | [5 empty] | Spare | [7 empty] | 0 | 0 | 0 |  |  | SPT2 09-09
9 | 8'8'12'12' | 28' D6L1/12' DX6LD |  |  | 0 | Produce 15-17,N12 | 45.6 | 20 | Off Cycle | 2.6 | 115 | 5.1 | 1.8 | 317 | 617 | 218.4 | 0 | 0 | SPRT2 09-09 | 180 | 1 3/8 | 1 5/8 | 5/8
10 |  |  |  |  | 0 | Spare | [12 empty] | SPRT2 09-09 |  |  |  | 1/2
11 | 12''8'8'4' | 28' D6L1/4' PF |  |  | 0 | Produce/Floral N10,N11,18,14 | 47.6 | 20 | Off Cycle | 2.8 | 115 | 3.3 |  | 340 | 398 | 0 |  |  | SPRT2 11-11 | 191 | 1 3/8 | 1 1/8 | 5/8
12 | [5 empty] | Spare | [7 empty] | 0 | 0 | 0 |  |  | SPRT2 07-07
13 | 8'8'12' | 28' LSB |  |  | 1 | Six Deck Meat 13-15 | 40.46 | 29 | Off Cycle | 4.6 | 120 | 4.11 | 0 | 552 | 493.2 | 0 | 0 | 0 | SPRT2 11-11 | 100 | 1 3/8 | 1 1/8 | 1/2
14 | 6'6'12'6'6' | 6'PT-72,6'PT-54,12'PTD54,6'PF-54,6'PT-54 |  |  | 0 | Deli 4-8 | 32.916 | 24 | Off Cycle | 5.33 | 115 | 8.22 | 0.62 | 612.95 | 945.3 | 71.3 | 0 | 0 | SPRT2 09-09 | 275 | 1 3/8 | 1 1/8 | 5/8
15 | [5 empty] | Spare | [7 empty] | 0 | 0 | 0 |  |  | SPRT2 05-07
16 | 7'X14'X9' | AA28-097 |  |  | 0 | Deli Cooler | 7.412 | 20 | Off Cycle | 4 | 115 | 0 | 0 | 480 | 0 | 0 | 0 | 0 | SPRT2 05-09 | 235 | 0.875 | 0.625 | 0.375
17 | 10'8'12' | 30' PT-72 |  |  | 0 | Cold Deli 1-3 | 31.62 | 24 | Off Cycle | 4.8 | 115 | 11.1 | 0 | 552 | 1276.5 | 0 | 0 | 0 | SPRT2 11-11 | 315 | 1 3/8 | 1 1/8 | 5/8
18 | [5 empty] | Future Beer | [7 empty] | 0 | 0 | 0 |  |  | SPRT2 11-11
19 | 24' | L6DLA | Retrofit Doors |  | 0 | Multi Deck Dairy44,45 | 14 | 30 | Off Cycle | 1.8 | 115 | 12.6 | 0 | 216 | 1512 | 0 | 0 | 0 | SPRT2 11-11 | 190 | 1 3/8 | 1 1/8 | 5/8
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  |  | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model #
Condensing Temp |  |  |  | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D.
Outside Air Temp. | [19 empty] | F P I
Required Load Group 1 |  |  | 0 | [16 empty] | Voltage
Comp. Capacity Group 1 |  |  | 0 | [16 empty] | FLA
Effective capac. with subcooling |  |  | 0 | [16 empty] | MCA
% Excess Capacity Group 1 | [19 empty] | MOPD
Rej. Heat (MBH) Group 1 |  |  | 0 | [16 empty] | Weight
|  |  | 0 | [16 empty] | Size
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 0 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 0 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 0 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size |  |  |  |  | Rev. | Date | By: |  |  | Revision: |  |  |  |  | Rev. | Date | By: |  | Revision:
Estimated Rack Weight Lbs.

## Remodel Rack A (Part 2)
Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack A | Existing | [12 empty] | Display Systems
2016 Gees Mill Road |  |  |  | Location: | ESSEX, MD |  |  |  | Rack Model: | [13 empty] | 1925 Ruffin Mill Road
Conyers, Georgia 30013 |  |  |  | Store #: | 1653 |  |  | Salesman |  | Kim Austin | [12 empty] | Colonial Heights, VA 23834
(770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: | 119439 |  |  | Prepared By: |  | Sandy Yon |  | Date Originated |  |  | 01/19/05 | [7 empty] | (804) 526-4455, Fax: (804) 526-1926
Rev. | Date | By: | Revision: | [7 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
A | 9/30/19 | J.Finch | Revised to new A1.01 Drawing. | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
A | 10/28/19 | DAB | Revised to new A1.01 Drawing. | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
[11 empty] | MCA |  |  |  | 311.675 |  |  | Fixture Plan:
[11 empty] | Max. Overcurrent |  |  |  | 400
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
20 | 36 | L6DLA | Retrofit Doors |  |  | Multi Deck Dairy 41-43 | 18 | 30 | TO | 5.4 | 115 | 6.3 |  | 648 | 756 | 0 | 0 | 0 | SPRT2 11-11 | 125 | 1 1/8 | 1.375 | 5/8
21 | 12 | L6DMA | Retrofit Doors |  |  | Multi Deck Dairy 39,40 | 6 | 30 | TO | 1.8 | 115 | 2.1 | 0 | 216 | 252 | 0 | 0 | 0 | SPRT2 09-09 | 90 | 7/8 | 7/8 | 5/8
22 | 8'8'8'8' | 16' L6DLA/16' DX6LD | Retrofit Doors |  |  | MD Dairy 37,38,N22,N23 | 12.8 | 28 | TO | 2.8 | 115 | 5.5 | 0 | 322 | 121 | 0 | 0 | 0 | SPRT2 09-09 | 235 | 7/8 | 5/8 | 5/8
23 | [5 empty] | Spare | [9 empty] | 0 | 0 | 0 | SPRT2 09-09
24 | 13'X36'X09' | 2)AA28-122 |  |  |  | Dairy Cooler | 23.344 | 20 | TO | 4 | 115 | 0 | 0 | 480 | 0 | 0 | 0 | 0 | SPRT2 09-09 | 85 | 1.125 | 0.875 | 0.375
25 | [5 empty] | Spare | [7 empty] | 0 | 0 | 0 |  |  | SPRT2 07-07
26 | 0 | 0 |  |  |  | Subcooling | 67.458 | 35 | TO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PORT2 11-11 | 20 | 1 1/8 |  | 0.5
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | VEQ 149
Condensing Temp |  |  | 115 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 11.9001 | 14.9
Outside Air Temp. |  |  | 100 |  | 1 | 06DM337 | 103.7 | 18 | 10 |  | 44.3 |  | 0 |  |  | 0 | 60A | 50A | #6 | F P I |  | 10
Required Load Group 1 |  |  | 557.539 | New | 2 | 06DM313 | 32.9 | 18 | 5 |  | 19.3 |  | 0 |  |  | 0 | 30A | 25A | #10 | Voltage |  | 208/60/3
Comp. Capacity Group 1 |  |  | 578.8 |  | 3 | 06EA565 | 178.4 | 18 | 25 |  | 90.7 | [5 empty] | 125A | 120A | #1 | FLA |  | 53
Effective capac. with subcooling |  |  | 578.8 |  | 4 | 06EM475 | 196.3 | 18 | 25 |  | 90.7 |  | 0 |  |  | 0 | 125A | 120A | #1 | MCA |  | 54.3
% Excess Capacity Group 1 |  |  | 3.813% | New | 5 | 06DR724 | 67.5 | 18 | 6.5 |  | 31.4 |  | 0 |  |  | 0 | 40A | 40A | #8 | MOPD |  | 70
Rej. Heat (MBH) Group 1 |  |  | 879.776 | [16 empty] | Weight |  | 2950
|  |  | 0 | [16 empty] | Size |  | 96"x242"
Required Load Group 2 |  |  | 0 |  |  |  |  | 0 | [11 empty] | # of Fans |  | 2x5 | 2x4
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 879.776 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 439.888 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out | [5 empty] | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 48.2 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size |  |  |  |  | Rev. | Date | By: |  |  | Revision: |  |  |  |  | Rev. | Date | By: |  | Revision:
Estimated Rack Weight Lbs.

## Remodel Rack B (Part 3)
Refrigeration Systems |  |  |  | Store / Cust: | Food Lion |  |  |  | Rack B | Existing | [12 empty] | Display Systems
2016 Gees Mill Road |  |  |  | Location: | ESSEX, MD |  |  |  | Rack Model: | [13 empty] | 1925 Ruffin Mill Road
Conyers, Georgia 30013 |  |  |  | Store #: | 1653 |  |  | Salesman |  | Kim Austin | [12 empty] | Colonial Heights, VA 23834
(770) 285-3264, Fax:(770) 285-3080 |  |  |  | Job #: | 119439 |  |  | Prepared By: |  | Sandy Yon |  | Date Originated |  |  | 01/19/05 | [7 empty] | (804) 526-4455, Fax: (804) 526-1926
Rev: | Date: | By: | Revision: | [7 empty] | Electrical Specs |  |  |  | Volt / Hz / Phase |  |  | Controller: |  |  |  | CPC
A1 | 9/30/19 | J.Finch | Revised to new A1.01 Drawing. | [7 empty] | Line |  |  |  | 208/60/3 |  |  | Single or Dual Point Pwr: |  |  |  | Single
A2 | 10/28/19 | DAB | Revised to new A1.01 Drawing. | [7 empty] | Control |  |  |  | 208/60/1 |  |  | Case Manufacturer
A3 | 1/7/2020 | RFF | Revised to walk notes | [7 empty] | MCA |  |  |  | 380.8 |  |  | Fixture Plan:
0 | 0 | 0 | 0 | [7 empty] | Max. Overcurrent |  |  |  | 450
Hill PHOENIX assumes no responsibility for the accuracy of the data presented herein. The user must field verify all information prior to installation.
Sys |  |  | Heat | Expansion | Temp |  | Load | Evap | Def | Fans |  | Amps @ 120V |  |  | Watts @ 120V |  | Refrig. Valves |  |  | Len. | Suction |  | Liquid
No | Size | Model | Exchr. | Valve | Probe | Application | Load | ° F | Type | Amps | Volts/1 | Lights | Htrs | Fans | Lights | Htrs | Hot Gas | Liquid | Suction | Run | Horiz | Riser | Horiz
1 | 10X11X09 | AG36-120 |  |  | 0 | Meat Freezer | 10.344 | -15 | HG | 3 | 208 | 0 | 0 | 690 | 0 | 0 |  | 0 | SPRT2 07-07 | 85 | 1 1/8 | 5/8 | 5/8
2 | 3 | 3Dr ORZ LED |  |  | 1 | Frozen Bakery 9 | 3.042 | -7 | HG 2 Wire | 1.5 | 120 | 0.5 | 2.78 | 180 | 60 | 333.6 |  |  | SPRT2 05-07 | 205 | 7/8 | 7/8 | 5/8
3 | 12X18X09 | AG46-164 |  |  | 0 | Bakery Freezer | 15.381 | -15 | HG | 4 | 208 | 0 | 0 | 920 | 0 | 0 |  | 0 | SPRT2 09-09 | 255 | 1 3/8 | 7/8 | 5/8
4 | 8'8' | LFW/IL1 |  |  | 0 | Meat Promo Dual Temp 24,22 | 6.8 | -25 | HG | 2.7 | 115 | 1.8 | 2 | 310 | 207 | 230 | 0 | 0 | SPRT2 05-07 | 105 | 1 1/8 | 0.875 | 0.625
5 | 21 Door | L5FGA/QIV5V14 |  |  | 0 | Reach-in Frozen Food 34-36,N20,N21 | 32.8 | -16 | HG | 7.3 | 115 | 14 | 34.8 | 840 | 1610 | 4002 | 0 | 0 | SPRT2 11-11 | 95 | 1 5/8 | 1.375 | 0.625
6 | 10 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 61,62 | 15.38 | -16 | HG | 7 | 115 | 13.6 | 6.4 | 840 | 1632 | 768 | 0 | 0 | SPRT2 09-09 | 110 | 1.125 | 0.875 | 0.625
7 | 10 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 63,64 | 15.38 | -16 | HG | 7 | 115 | 13.6 | 6.4 | 840 | 1632 | 768 | 0 | 0 | SPRT2 09-09 | 85 | 1.125 | 0.875 | 0.625
8 | 13 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 65-67 | 19.994 | -16 | HG | 9.2 | 115 | 17.8 | 8.5 | 1104 | 2136 | 1020 | 0 | 0 | SPRT2 09-09 | 70 | 1.125 | 0.875 | 0.625
9 | 15 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 58-60 | 23.07 | -16 | HG | 10.5 | 115 | 20.4 | 9.6 | 1260 | 2448 | 1152 | 0 | 0 | SPRT2 11-11 | 125 | 1.375 | 1.125 | 0.625
10 | 10 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 56,57 | 15.38 | -16 | HG | 7 | 115 | 13.6 | 6.4 | 840 | 1632 | 768 | 0 | 0 | SPRT2 09-09 | 90 | 1.125 | 0.875 | 0.625
11 | 14 Door | L5FGA |  |  | 0 | Reach-in Frozen Food 52-55 | 21.532 | -16 | HG | 9.8 | 115 | 19.1 | 9 | 1176 | 2292 | 1080 | 0 | 0 | SPRT2 11-11 | 80 | 1.125 | 0.875 | 0.625
12 | 14 Door | L5FGA |  |  | 0 | Reach-in Ice Cream 49-51 | 23.184 | -23 | HG | 9.8 | 115 | 19.1 | 9 | 1176 | 2292 | 1080 | 0 | 0 | SPRT2 11-11 | 110 | 1.375 | 1.125 | 0.625
13 | 13 Door | L5FGA |  |  | 0 | Reach-in Ice Cream 46-48 | 21.528 | -23 | HG | 9.2 | 115 | 17.8 | 8.5 | 1104 | 2136 | 1020 | 0 | 0 | SPRT2 11-11 | 130 | 1.375 | 1.125 | 0.625
14 | 12X35X09 | 2)AG36-140 |  |  | 0 | Grocery Freezer | 23.475 | -15 | HG | 6 | 208 | 0 | 0 | 1380 | 0 | 0 |  | 0 | SPRT2 11-11 | 110 | 1.375 | 1.125 | 0.625
15 | 12X15X09 | ITG24-325 |  | New | 0 | Ice Cream Freezer | 13.867 | -15 | HG | 6.4 | 208 | 0 | 0 | 1331.2 | 0 | 0 |  | 0 | SPRT2 09-09 | 80 | 1.125 | 0.875 | 0.625
16 | [5 empty] | Spare | [11 empty] | 0 | SPRT2 05-07
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
[14 empty] | 0 | 0 | 0
| General Specifications |  |  | Rack Model: |  |  |  |  | Compressor Specifications | [11 empty] | Condenser
Refrigerant Type |  |  | R-22 | Compressor | Comp |  |  | Suct |  |  |  |  | New Compressor |  |  | Capacity | Circuit |  | Wire Size | Model # |  | VEQ 91
Condensing Temp |  |  | 110 | Group # | # | Compressor | Cap | ° F | HP | RPM | RLA | LRA | Model |  |  | Control | Breaker | Contactor | (AWG) | T.D. |  | 9.7885
Outside Air Temp. |  |  | 100 |  | 1 | 06ER450 | 41.205 | -25 | 15 |  | 59.3 |  | 0 |  |  | 0 | 80A | 60A | #4 | F P I |  | 10
Required Load Group 1 |  |  | 261.157 |  | 2 | 06ER465 | 52.245 | -25 | 20 |  | 74.3 |  | 0 |  |  | 0 | 100A | 75A | #3 | Voltage |  | 208/60/3
Comp. Capacity Group 1 |  |  | 241.341 |  | 3 | 06ER475 | 65.759 | -25 | 20 |  | 74.3 |  | 0 |  |  | 0 | 100A | 75A | #3 | FLA |  | 31.8
Effective capac. with subcooling |  |  | 289.6092 |  | 4 | 06ER399 | 82.132 | -25 | 30 |  | 116.4 |  | 0 |  |  | 0 | 125A | 120A | #1 | MCA |  | 33.2
% Excess Capacity Group 1 |  |  | 10.89% | [16 empty] | MOPD |  | 40
Rej. Heat (MBH) Group 1 |  |  | 434.4138 | [16 empty] | Weight |  | 2050
|  |  | 0 | [16 empty] | Size |  | 96"x146"
Required Load Group 2 |  |  | 0 | [16 empty] | # of Fans
Comp. Capacity Group 2 |  |  | 0 | [16 empty] | Line To
Effective capac. with subcooling |  |  | 0 | [16 empty] | Line From
% Excess Capacity Group 2 | [8 empty] | Rack Components
Rej. Heat (MBH) Group 2 |  |  | 0 |  | Oil Separator -- Group 1 |  |  |  | Drain Regulator | [5 empty] | Air reclaim |  |  |  | Head Fan LT/MT
|  |  | 0 |  | Oil Separator -- Group 2 |  |  |  | Master Solenoid | [5 empty] | Water Reclaim |  |  |  | Crankcase Htrs.
Required Load Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 1 |  |  |  | Surge Solenoid | [5 empty] | Line size To
Comp. Capacity Group 3 |  |  | 0 |  | Disch. Check Valve -- Grp 2 |  |  |  | Surge Ball Valve | [5 empty] | Line size From
Effective capac. with subcooling |  |  | 0 |  | Disch. Reg. / Mas Liq |  |  |  | Surge Check | [5 empty] | Bypass Valve |  |  |  | Suction Crossover / Load Shed
% Excess Capacity Group 3 |  |  |  |  | Bypass Regulator |  |  |  | Surge Style | [5 empty] | Split Cond. Valve |  |  |  | Suction Group |  | 1 | 2 | 3
Rej. Heat (MBH) Group 3 |  |  | 0 |  | Oil Filter |  |  |  | Attron | [5 empty] | Ext. Cond. Bleed |  |  |  | Ball Valve
|  |  | 0 |  | Brand / Number | [9 empty] | Receiver H / V |  |  |  | Check Valve
Total Rej. Heat (MBH) |  |  | 434.4138 |  | Suction Filter -- Group 1 |  |  |  | Subcooler | [5 empty] | Dia. x Length |  |  |  | Solenoid
Heat Reclaim Avail. (MBH) |  |  | 217.2069 |  | Suction Filter -- Group 2 |  |  |  | Liquid Temp Out |  |  | 50º |  |  | Lbs @ 90% PD |  |  |  | C P R
Compressor Capacity (Tons) |  |  | 20.1 |  | Drier |  |  |  | TEV | [9 empty] | From / To
Rack Size |  |  |  |  | Rev. | Date | By: |  |  | Revision: |  |  |  |  | Rev. | Date | By: |  | Revision:
Estimated Rack Weight Lbs.